## Descriptions
AGC 200 Modbus 描述
软件版本
这些表中所包含的信息适用于AGC 200 产品4.68.2软件版本。
行 | 超链接索引
13 | Modbus 功能码
24 | 离散型输出线圈
32 | 离散型输入输出
41 | 输出保持寄存器
50 | 输入寄存器
返回到索引 | Modbus 功能码
| 功能码 | 描述
| 01 | 读单个或多个离散型线圈
| 02 | 读单个或多个离散型输入点
| 03 | 读单个或多个保持寄存器
| 04 | 读单个或多个输入寄存器.
| 05 | 向单个离散型输出线圈写入一个值。
| 06 | 写一个值到单个的输出寄存器.
| 15 | 写值到多个连续的离散型线圈
| 16 | 写值到多个连续的输出寄存器
返回到索引 | 离散型输出线圈
| 功能码 | 用途
| 01 | 读
| 05 或 15 | 写
| 功能组 | 描述
| 命令标志位 | 在控制器中激活命令. 读：控制器始终返回0 (false). 写：控制器执行命令如果你写1(true).
返回到索引 | 离散型输入输出
| 功能码 | 用途
| 02 | 读
| 功能组 | 描述
| 状态标志位 | 读是否一个状态标志位被激活了 当状态标志位未激活这控制器返回值0（false） 当状态标志位激活这控制器返回值1（true）
| 开关量输入 | 读 控制器开关量输入状态 当开关量输入未激活这控制器返回值0（false） 当开关量输入激活这控制器返回值1（true）
| 开关量输出 | 读控制器开关量输出状态 当开关量输出未激活这控制器返回值0（false） 当开关量输出激活这控制器返回值1（true）
返回到索引 | 输出保持寄存器
| 功能码 | 用途
| 03 | 读
| 06 或 16 | 写
| 功能组 | 描述
| 控制命令 | 在控制器中激活命令. 读：控制器始终返回0（false）来自这地址位 写：这控制器执行这命令如果你写1(true)到这地址位
| 控制时间命令 | 读取和写入这控制器时间和日期值 读：控制器返回相关功能的返回值 写：控制器改变相关功能的值如果一个有效值被输入
返回到索引 | 输入寄存器
| 功能码 | 用途
| 04 | 读
| 功能组 | 描述
| AC 测量 | 读取相关交流测量的操作值
| 报警 | 读某位看是否这报警被激活了 当未有报警被激活时，控制器返回0 (false) 当有报警被激活时，控制器返回1 (true)
| 功率管理(PM) 交流测量 | 读取与电站管理测量和设置相关的值
| 功率管理(PM)报警 | 读取1位看是否与功率管理状态或报警被激活了 当状态/报警未被激活时，控制器返回0 (false)。 当状态/报警被激活时，控制器返回1 (true)

## Discrete output coil (01;05;15)
离散型输出线圈 (01;05;15)
功能组 | Modbus 地址 | PLC地址 | Modbus 功能码 | 注解 | BTB单元 | 主网单元 | 机组单元
命令标志位 | 0 | 1 | 01; 05; 15 | 遥控启动（半自动状态） |  |  | X
命令标志位 | 1 | 2 | 01; 05; 15 | 遥控机组合闸（半自动状态） |  |  | X
命令标志位 | 1 | 2 | 01; 05; 15 | 遥控BTB合闸（半自动状态） | X
命令标志位 | 1 | 2 | 01; 05; 15 | 遥控TB合闸（半自动状态） |  | X
命令标志位 | 2 | 3 | 01; 05; 15 | 遥控机组分闸（半自动模式下有效） |  |  | X
命令标志位 | 2 | 3 | 01; 05; 15 | 遥控BTB分闸（半自动模式下有效） | X
命令标志位 | 2 | 3 | 01; 05; 15 | 遥控TB分闸（半自动模式下有效） |  | X
命令标志位 | 3 | 4 | 01; 05; 15 | 遥控机组停机 |  |  | X
命令标志位 | 4 | 5 | 01; 05; 15 | 激活报警抑制1 | X | X | X
命令标志位 | 5 | 6 | 01; 05; 15 | 报警抑制2 | X | X | X
命令标志位 | 6 | 7 | 01; 05; 15 | 激活报警抑制3 | X | X | X
命令标志位 | 7 | 8 | 01; 05; 15 | 复位调速GOV/调压AVR调节输出偏置 |  |  | X
命令标志位 | 9 | 10 | 01; 05; 15 | 全部报警复位 | X | X | X
命令标志位 | 10 | 11 | 01; 05; 15 | 额定参数组1选择 | X | X | X
命令标志位 | 11 | 12 | 01; 05; 15 | 额定参数组2选择 | X | X | X
命令标志位 | 12 | 13 | 01; 05; 15 | 额定参数组3选择 | X | X | X
命令标志位 | 13 | 14 | 01; 05; 15 | 额定参数组4选择 | X | X | X
命令标志位 | 14 | 15 | 01; 05; 15 | 启动+同步 (半自动) |  |  | X
命令标志位 | 15 | 16 | 01; 05; 15 | 解列/停机 (半自动) |  |  | X
命令标志位 | 16 | 17 | 01; 05; 15 | 孤岛 |  | X | X
命令标志位 | 17 | 18 | 01; 05; 15 | 自动市电失效(AMF) |  | X | X
命令标志位 | 18 | 19 | 01; 05; 15 | 调峰（Peak shaving） |  | X | X
命令标志位 | 19 | 20 | 01; 05; 15 | 固定功率 |  | X | X
命令标志位 | 20 | 21 | 01; 05; 15 | 市电输出(MPE) |  | X | X
命令标志位 | 21 | 22 | 01; 05; 15 | 负载轮换（机组-主网之间）(LTO) |  | X | X
命令标志位 | 24 | 25 | 01; 05; 15 | 遥控市电(主网）合闸（仅市电单元） |  | X | X
命令标志位 | 25 | 26 | 01; 05; 15 | 遥控市电(主网）分闸（仅市电单元） |  | X | X
命令标志位 | 26 | 27 | 01; 05; 15 | 自动起停（自动模式） |  | X | X
命令标志位 | 27 | 28 | 01; 05; 15 | 手动模式（Man） |  |  | X
命令标志位 | 28 | 29 | 01; 05; 15 | 半自动模式（Semi） | X | X | X
命令标志位 | 29 | 30 | 01; 05; 15 | 自动模式（Auto） | X | X | X
命令标志位 | 30 | 31 | 01; 05; 15 | 测试模式（Test） |  | X | X
命令标志位 | 31 | 32 | 01; 05; 15 | 外部频率控制 |  |  | X
命令标志位 | 32 | 33 | 01; 05; 15 | 外部电压控制（接收外部电压或其它信号输入） |  |  | X
命令标志位 | 33 | 34 | 01; 05; 15 | 外部有功控制（接收外部电压或其它信号输入） |  | X | X
命令标志位 | 34 | 35 | 01; 05; 15 | 外部无功控制（接收外部电压或其它信号输入） |  |  | X
命令标志位 | 35 | 36 | 01; 05; 15 | 外部功率因素控制（接收外部电压或其它信号输入） |  |  | X
命令标志位 | 36 | 37 | 01; 05; 15 | 容性功率因数 |  |  | X
命令标志位 | 37 | 38 | 01; 05; 15 | 基本负载（Base load） |  |  | X
命令标志位 | 38 | 39 | 01; 05; 15 | 第一优先级选择 |  |  | X
命令标志位 | 40 | 41 | 01; 05; 15 | 应用1选择 | X | X | X
命令标志位 | 41 | 42 | 01; 05; 15 | 应用2选择 | X | X | X
命令标志位 | 42 | 43 | 01; 05; 15 | 应用3选择 | X | X | X
命令标志位 | 43 | 44 | 01; 05; 15 | 应用4选择 | X | X | X
命令标志位 | 44 | 45 | 01; 05; 15 | 电池测试激活 |  |  | X
命令标志位 | 46 | 47 | 01; 05; 15 | 同步时钟到 4:00 a.m. | X | X | X
命令标志位 | 48 | 49 | 01; 05; 15 | 虚拟事件激活 1 | X | X | X
命令标志位 | 49 | 50 | 01; 05; 15 | 虚拟事件激活 2 | X | X | X
命令标志位 | 50 | 51 | 01; 05; 15 | 虚拟事件激活 3 | X | X | X
命令标志位 | 51 | 52 | 01; 05; 15 | 虚拟事件激活 4 | X | X | X
命令标志位 | 52 | 53 | 01; 05; 15 | 虚拟事件激活 5 | X | X | X
命令标志位 | 53 | 54 | 01; 05; 15 | 虚拟事件激活 6 | X | X | X
命令标志位 | 54 | 55 | 01; 05; 15 | 虚拟事件激活 7 | X | X | X
命令标志位 | 55 | 56 | 01; 05; 15 | 虚拟事件激活 8 | X | X | X
命令标志位 | 56 | 57 | 01; 05; 15 | 虚拟事件激活 9 | X | X | X
命令标志位 | 57 | 58 | 01; 05; 15 | 虚拟事件激活 10 | X | X | X
命令标志位 | 58 | 59 | 01; 05; 15 | 虚拟事件激活 11 | X | X | X
命令标志位 | 59 | 60 | 01; 05; 15 | 虚拟事件激活 12 | X | X | X
命令标志位 | 60 | 61 | 01; 05; 15 | 虚拟事件激活 13 | X | X | X
命令标志位 | 61 | 62 | 01; 05; 15 | 虚拟事件激活 14 | X | X | X
命令标志位 | 62 | 63 | 01; 05; 15 | 虚拟事件激活 15 | X | X | X
命令标志位 | 63 | 64 | 01; 05; 15 | 虚拟事件激活 16 | X | X | X
命令标志位 | 64 | 65 | 01; 05; 15 | 虚拟事件激活 17 | X | X | X
命令标志位 | 65 | 66 | 01; 05; 15 | 虚拟事件激活 18 | X | X | X
命令标志位 | 66 | 67 | 01; 05; 15 | 虚拟事件激活 19 | X | X | X
命令标志位 | 67 | 68 | 01; 05; 15 | 虚拟事件激活 20 | X | X | X
命令标志位 | 68 | 69 | 01; 05; 15 | 虚拟事件激活 21 | X | X | X
命令标志位 | 69 | 70 | 01; 05; 15 | 虚拟事件激活 22 | X | X | X
命令标志位 | 70 | 71 | 01; 05; 15 | 虚拟事件激活 23 | X | X | X
命令标志位 | 71 | 72 | 01; 05; 15 | 虚拟事件激活 24 | X | X | X
命令标志位 | 72 | 73 | 01; 05; 15 | 虚拟事件激活 25 | X | X | X
命令标志位 | 73 | 74 | 01; 05; 15 | 虚拟事件激活 26 | X | X | X
命令标志位 | 74 | 75 | 01; 05; 15 | 虚拟事件激活 27 | X | X | X
命令标志位 | 75 | 76 | 01; 05; 15 | 虚拟事件激活 28 | X | X | X
命令标志位 | 76 | 77 | 01; 05; 15 | 虚拟事件激活 29 | X | X | X
命令标志位 | 77 | 78 | 01; 05; 15 | 虚拟事件激活 30 | X | X | X
命令标志位 | 78 | 79 | 01; 05; 15 | 虚拟事件激活 31 | X | X | X
命令标志位 | 79 | 80 | 01; 05; 15 | 虚拟事件激活 32 | X | X | X
命令标志位 | 121 | 122 | 01; 05; 15 | 清除历史记录 | X | X | X
命令标志位 | 122 | 123 | 01; 05; 15 | 清除参数编辑（带笔的标志） | X | X | X
命令标志位 | 123 | 124 | 01; 05; 15 | 使能外部频率控制 |  |  | X
命令标志位 | 124 | 125 | 01; 05; 15 | 不使能外部频率控制 |  |  | X
命令标志位 | 125 | 126 | 01; 05; 15 | 使能外部电压控制 |  |  | X
命令标志位 | 126 | 127 | 01; 05; 15 | 不使能外部电压控制 |  |  | X
命令标志位 | 127 | 128 | 01; 05; 15 | 使能外部有功控制 |  | X | X
命令标志位 | 128 | 129 | 01; 05; 15 | 不使能外部有功控制 |  | X | X
命令标志位 | 129 | 130 | 01; 05; 15 | 使能外部无功控制 |  |  | X
命令标志位 | 130 | 131 | 01; 05; 15 | 不使能外部无功控制 |  |  | X
命令标志位 | 131 | 132 | 01; 05; 15 | 使能外部功率因数控制 |  |  | X
命令标志位 | 132 | 133 | 01; 05; 15 | 不使能外部功率因数控制 |  |  | X
命令标志位 | 133 | 134 | 01; 05; 15 | 使能PM基本负载（base load）控制 |  |  | X
命令标志位 | 134 | 135 | 01; 05; 15 | 不使能PM基本负载（base load）控制 |  |  | X
命令标志位 | 135 | 136 | 01; 05; 15 | 消音 | X | X | X
命令标志位 | 137 | 138 | 01; 05; 15 | DVC 310/510:复位报警 |  |  | X
命令标志位 | 138 | 139 | 01; 05; 15 | EIC：改变DM1缓冲（Change DM1 buffer） |  |  | X
命令标志位 | 139 | 140 | 01; 05; 15 | EIC：请求DM2历史记录（Request DM2） |  |  | X
命令标志位 | 140 | 141 | 01; 05; 15 | EIC：改变次要DM1缓冲（Change secondary DM1 buffer） |  |  | X
命令标志位 | 141 | 142 | 01; 05; 15 | EIC：请求KWP2000历史记录（Request KWP2000） |  |  | X
Note on A4: More information about each function group is available in the description sheet.
Note on D4: 01 - Read single or multiple 05 - Write single 15 - Write multiple
Note on E4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on F4: Indicates if the address is available in the BUS TIE breaker controller.
Note on G4: Indicates if the address is available in the MAINS controller.
Note on H4: Indicates if the address is available in the GENSET controller.

## Discrete input contact (02)
离散型输入输出（02）
功能组 | Modbus 地址 | PLC地址 | Modbus 功能码 | 注解 | BTB单元 | 主网单元 | 机组单元
状态标志位 | 1 | 100002 | 2 | 市电位置反馈ON |  | X | X
状态标志位 | 3 | 100004 | 2 | 运行 |  |  | X
状态标志位 | 4 | 100005 | 2 | 发电机电压/频率OK |  |  | X
状态标志位 | 4 | 100005 | 2 | 母排电压/频率OK |  | X
状态标志位 | 4 | 100005 | 2 | Busbar B 电压/频率OK | X
状态标志位 | 5 | 100006 | 2 | 市电(主网)故障 |  | X | X
状态标志位 | 6 | 100007 | 2 | 检修模式（Block mode） |  |  | X
状态标志位 | 7 | 100008 | 2 | 手动模式（Man） |  |  | X
状态标志位 | 8 | 100009 | 2 | 半自动模式（Semi） | X | X | X
状态标志位 | 9 | 100010 | 2 | 自动模式（Auto） | X | X | X
状态标志位 | 10 | 100011 | 2 | 测试模式（Test） |  | X | X
状态标志位 | 13 | 100014 | 2 | 孤岛 |  | X | X
状态标志位 | 14 | 100015 | 2 | 自动市电失效(AMF) |  | X | X
状态标志位 | 15 | 100016 | 2 | 调峰（Peak shaving） |  | X | X
状态标志位 | 16 | 100017 | 2 | 固定功率 |  | X | X
状态标志位 | 17 | 100018 | 2 | 市电输出(MPE) |  | X | X
状态标志位 | 18 | 100019 | 2 | 负载轮换（机组-主网之间）(LTO) |  | X | X
状态标志位 | 19 | 100020 | 2 | 功率管理（Power management） |  |  | X
状态标志位 | 20 | 100021 | 2 | 在PMS ID1存在报警 | X | X | X
状态标志位 | 21 | 100022 | 2 | 在PMS ID2存在报警 | X | X | X
状态标志位 | 22 | 100023 | 2 | 在PMS ID3存在报警 | X | X | X
状态标志位 | 23 | 100024 | 2 | 在PMS ID4存在报警 | X | X | X
状态标志位 | 24 | 100025 | 2 | 在PMS ID5存在报警 | X | X | X
状态标志位 | 25 | 100026 | 2 | 在PMS ID6存在报警 | X | X | X
状态标志位 | 26 | 100027 | 2 | 在PMS ID7存在报警 | X | X | X
状态标志位 | 27 | 100028 | 2 | 在PMS ID8存在报警 | X | X | X
状态标志位 | 28 | 100029 | 2 | 任一市电（主网）报警(市电（主网)单元） | X | X | X
状态标志位 | 29 | 100030 | 2 | 电池测试激活 |  |  | X
状态标志位 | 31 | 100032 | 2 | DG1自动起动准备就绪 | X | X | X
状态标志位 | 32 | 100033 | 2 | DG2自动起动准备就绪 | X | X | X
状态标志位 | 33 | 100034 | 2 | DG3自动起动准备就绪 | X | X | X
状态标志位 | 34 | 100035 | 2 | DG4自动起动准备就绪 | X | X | X
状态标志位 | 35 | 100036 | 2 | DG5自动起动准备就绪 | X | X | X
状态标志位 | 36 | 100037 | 2 | DG6自动起动准备就绪 | X | X | X
状态标志位 | 37 | 100038 | 2 | DG7自动起动准备就绪 | X | X | X
状态标志位 | 38 | 100039 | 2 | DG8自动起动准备就绪 | X | X | X
状态标志位 | 53 | 100054 | 2 | 市电（主网）同步禁止 |  | X | X
状态标志位 | 54 | 100055 | 2 | 任一市电（主网）同步禁止 | X | X | X
状态标志位 | 518 | 100519 | 2 | TB 合闸反馈点 |  | X
状态标志位 | 518 | 100519 | 2 | GB位置反馈ON |  |  | X
状态标志位 | 518 | 100519 | 2 | BTB 合闸反馈点 | X
开关量输入 | 22500 | 122501 | 2 | 输入点状态位 77 | X | X | X
开关量输入 | 22501 | 122502 | 2 | 输入点状态位 78 | X | X | X
开关量输入 | 22502 | 122503 | 2 | 输入点状态位 79 | X | X | X
开关量输入 | 22503 | 122504 | 2 | 输入点状态位 80 | X | X | X
开关量输入 | 22504 | 122505 | 2 | 输入点状态位 81 | X | X | X
开关量输入 | 22505 | 122506 | 2 | 输入点状态位 82 | X | X | X
开关量输入 | 22506 | 122507 | 2 | 输入点状态位 83 | X | X | X
开关量输入 | 22507 | 122508 | 2 | 输入点状态位 84 | X | X | X
开关量输入 | 22508 | 122509 | 2 | 输入点状态位 85 | X | X | X
开关量输入 | 22509 | 122510 | 2 | 输入点状态位 86 | X | X | X
开关量输入 | 22515 | 122516 | 2 | 停机线圈断线 |  |  | X
开关量输入 | 22516 | 122517 | 2 | 急停信号 | X | X | X
开关量输入 | 22591 | 122592 | 2 | 开关量输入 48 | X | X | X
开关量输入 | 22592 | 122593 | 2 | 开关量输入 47 | X | X | X
开关量输入 | 22593 | 122594 | 2 | 开关量输入 46 | X | X | X
开关量输入 | 22594 | 122595 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 10 | X | X | X
开关量输入 | 22595 | 122596 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 11 | X | X | X
开关量输入 | 22596 | 122597 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 12 | X | X | X
开关量输入 | 22597 | 122598 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 13 | X | X | X
开关量输入 | 22598 | 122599 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 14 | X | X | X
开关量输入 | 22599 | 122600 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 15 | X | X | X
开关量输入 | 22600 | 122601 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 16 | X | X | X
开关量输入 | 22601 | 122602 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 17 | X | X | X
开关量输入 | 22602 | 122603 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 19 | X | X | X
开关量输入 | 22603 | 122604 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 20 | X | X | X
开关量输入 | 22604 | 122605 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 21 | X | X | X
开关量输入 | 22605 | 122606 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 22 | X | X | X
开关量输入 | 22606 | 122607 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 23 | X | X | X
开关量输入 | 22607 | 122608 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 24 | X | X | X
开关量输入 | 22608 | 122609 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 25 | X | X | X
开关量输入 | 22609 | 122610 | 2 | 扩展输入点状态位/CIO 116 no. 1.输入 26 | X | X | X
开关量输入 | 22610 | 122611 | 2 | CIO 116 no. 2.输入 10 | X | X | X
开关量输入 | 22611 | 122612 | 2 | CIO 116 no. 2.输入 11 | X | X | X
开关量输入 | 22612 | 122613 | 2 | CIO 116 no. 2.输入 12 | X | X | X
开关量输入 | 22613 | 122614 | 2 | CIO 116 no. 2.输入 13 | X | X | X
开关量输入 | 22614 | 122615 | 2 | CIO 116 no. 2.输入 14 | X | X | X
开关量输入 | 22615 | 122616 | 2 | CIO 116 no. 2.输入 15 | X | X | X
开关量输入 | 22616 | 122617 | 2 | CIO 116 no. 2.输入 16 | X | X | X
开关量输入 | 22617 | 122618 | 2 | CIO 116 no. 2.输入 17 | X | X | X
开关量输入 | 22618 | 122619 | 2 | CIO 116 no. 2.输入 19 | X | X | X
开关量输入 | 22619 | 122620 | 2 | CIO 116 no. 2.输入 20 | X | X | X
开关量输入 | 22620 | 122621 | 2 | CIO 116 no. 2.输入 21 | X | X | X
开关量输入 | 22621 | 122622 | 2 | CIO 116 no. 2.输入 22 | X | X | X
开关量输入 | 22622 | 122623 | 2 | CIO 116 no. 2.输入 23 | X | X | X
开关量输入 | 22623 | 122624 | 2 | CIO 116 no. 2.输入 24 | X | X | X
开关量输入 | 22624 | 122625 | 2 | CIO 116 no. 2.输入 25 | X | X | X
开关量输入 | 22625 | 122626 | 2 | CIO 116 no. 2.输入 26 | X | X | X
开关量输入 | 22626 | 122627 | 2 | CIO 116 no. 3.输入 10 | X | X | X
开关量输入 | 22627 | 122628 | 2 | CIO 116 no. 3.输入 11 | X | X | X
开关量输入 | 22628 | 122629 | 2 | CIO 116 no. 3.输入 12 | X | X | X
开关量输入 | 22629 | 122630 | 2 | CIO 116 no. 3.输入 13 | X | X | X
开关量输入 | 22630 | 122631 | 2 | CIO 116 no. 3.输入 14 | X | X | X
开关量输入 | 22631 | 122632 | 2 | CIO 116 no. 3.输入 15 | X | X | X
开关量输入 | 22632 | 122633 | 2 | CIO 116 no. 3.输入 16 | X | X | X
开关量输入 | 22633 | 122634 | 2 | CIO 116 no. 3.输入 17 | X | X | X
开关量输入 | 22634 | 122635 | 2 | CIO 116 no. 3.输入 19 | X | X | X
开关量输入 | 22635 | 122636 | 2 | CIO 116 no. 3.输入 20 | X | X | X
开关量输入 | 22636 | 122637 | 2 | CIO 116 no. 3.输入 21 | X | X | X
开关量输入 | 22637 | 122638 | 2 | CIO 116 no. 3.输入 22 | X | X | X
开关量输入 | 22638 | 122639 | 2 | CIO 116 no. 3.输入 23 | X | X | X
开关量输入 | 22639 | 122640 | 2 | CIO 116 no. 3.输入 24 | X | X | X
开关量输入 | 22640 | 122641 | 2 | CIO 116 no. 3.输入 25 | X | X | X
开关量输入 | 22641 | 122642 | 2 | CIO 116 no. 3.输入 26 | X | X | X
开关量输出 | 23001 | 123002 | 2 | 继电器 16 | X | X | X
开关量输出 | 23002 | 123003 | 2 | 继电器 18 | X | X | X
开关量输出 | 23003 | 123004 | 2 | 继电器 20 | X | X | X
开关量输出 | 23004 | 123005 | 2 | 继电器 23 | X | X | X
开关量输出 | 23005 | 123006 | 2 | 继电器 26 | X | X | X
开关量输出 | 23006 | 123007 | 2 | 继电器 27 | X | X | X
开关量输出 | 23007 | 123008 | 2 | 继电器 28 | X | X | X
开关量输出 | 23008 | 123009 | 2 | 继电器 30 | X | X | X
开关量输出 | 23009 | 123010 | 2 | 继电器 32 | X | X | X
开关量输出 | 23010 | 123011 | 2 | 继电器 34 | X | X | X
开关量输出 | 23011 | 123012 | 2 | 继电器 36 | X | X | X
开关量输出 | 23012 | 123013 | 2 | 继电器 39 | X | X | X
开关量输出 | 23013 | 123014 | 2 | 继电器 41 | X | X | X
开关量输出 | 23014 | 123015 | 2 | 继电器 43 | X | X | X
开关量输出 | 23056 | 123057 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出9 | X | X | X
开关量输出 | 23057 | 123058 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出11 | X | X | X
开关量输出 | 23058 | 123059 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出13 | X | X | X
开关量输出 | 23059 | 123060 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出15 | X | X | X
开关量输出 | 23060 | 123061 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出18 | X | X | X
开关量输出 | 23061 | 123062 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出21 | X | X | X
开关量输出 | 23062 | 123063 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出24 | X | X | X
开关量输出 | 23063 | 123064 | 2 | 扩展 输出继电器状态位/CIO 208 no. 1.输出27 | X | X | X
开关量输出 | 23064 | 123065 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出9 | X | X | X
开关量输出 | 23065 | 123066 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出11 | X | X | X
开关量输出 | 23066 | 123067 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出13 | X | X | X
开关量输出 | 23067 | 123068 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出15 | X | X | X
开关量输出 | 23068 | 123069 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出18 | X | X | X
开关量输出 | 23069 | 123070 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出21 | X | X | X
开关量输出 | 23070 | 123071 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出24 | X | X | X
开关量输出 | 23071 | 123072 | 2 | 扩展 输出继电器状态位/CIO 208 no. 2.输出27 | X | X | X
开关量输出 | 23072 | 123073 | 2 | CIO 208 no. 3.输出9 | X | X | X
开关量输出 | 23073 | 123074 | 2 | CIO 208 no. 3.输出11 | X | X | X
开关量输出 | 23074 | 123075 | 2 | CIO 208 no. 3.输出13 | X | X | X
开关量输出 | 23075 | 123076 | 2 | CIO 208 no. 3.输出15 | X | X | X
开关量输出 | 23076 | 123077 | 2 | CIO 208 no. 3.输出18 | X | X | X
开关量输出 | 23077 | 123078 | 2 | CIO 208 no. 3.输出21 | X | X | X
开关量输出 | 23078 | 123079 | 2 | CIO 208 no. 3.输出24 | X | X | X
开关量输出 | 23079 | 123080 | 2 | CIO 208 no. 3.输出27 | X | X | X
开关量输出 | 23080 | 123081 | 2 | CIO 116 no. 1 可配置自检状态输出 | X | X | X
开关量输出 | 23081 | 123082 | 2 | CIO 116 no. 2 可配置自检状态输出 | X | X | X
开关量输出 | 23082 | 123083 | 2 | CIO 116 no. 3 可配置自检状态输出 | X | X | X
开关量输出 | 23083 | 123084 | 2 | CIO 208 no. 1 可配置自检状态输出 | X | X | X
开关量输出 | 23084 | 123085 | 2 | CIO 208 no. 2 可配置自检状态输出 | X | X | X
开关量输出 | 23085 | 123086 | 2 | CIO 208 no. 3 可配置自检状态输出 | X | X | X
开关量输出 | 23086 | 123087 | 2 | CIO 308 no. 1 可配置自检状态输出 | X | X | X
开关量输出 | 23087 | 123088 | 2 | CIO 308 no. 2 可配置自检状态输出 | X | X | X
开关量输出 | 23088 | 123089 | 2 | CIO 308 no. 3 可配置自检状态输出 | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on D4: 02 - Read single or multiple
Note on E4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on F4: Indicates if the address is available in the BUS TIE breaker controller.
Note on G4: Indicates if the address is available in the MAINS controller.
Note on H4: Indicates if the address is available in the GENSET controller.

## Holding register (03;06;16)
保持寄存器 (03;06;16)
功能组 | Modbus 地址 | 位 | PLC地址 | Modbus 功能码 | 注解 | 数据类型 | 数据格式 | 比例 (10⁻ˣ) | 单位 | BTB单元 | 主网单元 | 机组单元
控制命令 | 0 |  | 400001 | 03; 06; 16 | 有功功率调节设定点--- 0...100%额定功率.在菜单7501激活 | INT16s | AB | 0 |  |  | X | X
控制命令 | 1 |  | 400002 | 03; 06; 16 | 功率因数设定点--- 60...100 表示为功率因数值/100.这值100意味着功率因数 = 1.00 在菜单7504激活 | INT16s | AB | 0 |  |  |  | X
控制命令 | 2 |  | 400003 | 03; 06; 16 | 无功功率设定点--- +/-100% 额定功率.一个负值意味着容性负载, 一个正值意味着感性负载.在菜单7505激活 | INT16s | AB | 0 |  |  |  | X
控制命令 | 3 |  | 400004 | 03; 06; 16 | 频率设定点--- +/-100%对应于 +/10.0% 的额定频率.在菜单7502激活 | INT16s | AB | 0 |  |  |  | X
控制命令 | 4 |  | 400005 | 03; 06; 16 | 电压调节设定点--- +/-100% 对应于+/10.0%额定频率.在菜单7503激活 | INT16s | AB | 0 |  |  |  | X
控制命令 | 5 | 0 | 400006 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 5 | 1 | 400006 | 03; 06; 16 | 遥控启动（半自动模式下有效） | BOOL | [5 empty] | X
控制命令 | 5 | 2 | 400006 | 03; 06; 16 | 遥控机组合闸（半自动状态） | BOOL | [5 empty] | X
控制命令 | 5 | 2 | 400006 | 03; 06; 16 | 遥控BTB合闸（半自动状态） | BOOL |  |  |  | X
控制命令 | 5 | 2 | 400006 | 03; 06; 16 | 遥控TB合闸（半自动状态） | BOOL |  |  |  |  | X
控制命令 | 5 | 3 | 400006 | 03; 06; 16 | 遥控机组分闸（半自动模式下有效） | BOOL | [5 empty] | X
控制命令 | 5 | 3 | 400006 | 03; 06; 16 | 遥控BTB分闸（半自动模式下有效） | BOOL |  |  |  | X
控制命令 | 5 | 3 | 400006 | 03; 06; 16 | 遥控TB分闸（半自动模式下有效） | BOOL |  |  |  |  | X
控制命令 | 5 | 4 | 400006 | 03; 06; 16 | 遥控机组停机 | BOOL | [5 empty] | X
控制命令 | 5 | 5 | 400006 | 03; 06; 16 | 复位调速GOV/调压AVR调节输出偏置 | BOOL | [5 empty] | X
控制命令 | 5 | 6 | 400006 | 03; 06; 16 | 启动+同步 (半自动) | BOOL | [5 empty] | X
控制命令 | 5 | 7 | 400006 | 03; 06; 16 | 激活报警抑制1 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 8 | 400006 | 03; 06; 16 | 报警抑制2 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 9 | 400006 | 03; 06; 16 | 激活报警抑制3 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 10 | 400006 | 03; 06; 16 | 全部报警复位 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 11 | 400006 | 03; 06; 16 | 额定参数组1选择 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 12 | 400006 | 03; 06; 16 | 额定参数组2选择 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 13 | 400006 | 03; 06; 16 | 额定参数组3选择 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 14 | 400006 | 03; 06; 16 | 额定参数组4选择 | BOOL |  |  |  | X | X | X
控制命令 | 5 | 15 | 400006 | 03; 06; 16 | 解列/停机 (半自动) | BOOL | [5 empty] | X
控制命令 | 6 | 0 | 400007 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 6 | 1 | 400007 | 03; 06; 16 | 孤岛模式(Island) | BOOL |  |  |  |  | X | X
控制命令 | 6 | 2 | 400007 | 03; 06; 16 | 自动市电失效(AMF) | BOOL |  |  |  |  | X | X
控制命令 | 6 | 3 | 400007 | 03; 06; 16 | 调峰（Peak shaving） | BOOL |  |  |  |  | X | X
控制命令 | 6 | 4 | 400007 | 03; 06; 16 | 固定功率 | BOOL |  |  |  |  | X | X
控制命令 | 6 | 5 | 400007 | 03; 06; 16 | 市电输出(MPE) | BOOL |  |  |  |  | X | X
控制命令 | 6 | 6 | 400007 | 03; 06; 16 | 负载轮换（机组-主网之间）(LTO) | BOOL |  |  |  |  | X | X
控制命令 | 6 | 9 | 400007 | 03; 06; 16 | 遥控市电(主网）合闸(单机模式) | BOOL | [5 empty] | X
控制命令 | 6 | 9 | 400007 | 03; 06; 16 | 遥控市电(主网）合闸（仅市电单元） | BOOL |  |  |  |  | X
控制命令 | 6 | 10 | 400007 | 03; 06; 16 | 遥控市电(主网）分闸(单机模式) | BOOL | [5 empty] | X
控制命令 | 6 | 10 | 400007 | 03; 06; 16 | 遥控市电(主网）分闸（仅市电单元） | BOOL |  |  |  |  | X
控制命令 | 6 | 11 | 400007 | 03; 06; 16 | 自动起停（自动模式） | BOOL |  |  |  |  | X | X
控制命令 | 6 | 12 | 400007 | 03; 06; 16 | 手动模式（Man） | BOOL | [5 empty] | X
控制命令 | 6 | 13 | 400007 | 03; 06; 16 | 自动模式（Auto） | BOOL |  |  |  | X | X | X
控制命令 | 6 | 14 | 400007 | 03; 06; 16 | 半自动模式（Semi） | BOOL |  |  |  | X | X | X
控制命令 | 6 | 15 | 400007 | 03; 06; 16 | 测试模式（Test） | BOOL |  |  |  |  | X | X
控制命令 | 7 | 0 | 400008 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 7 | 1 | 400008 | 03; 06; 16 | 外部频率控制（接收外部电压或其它信号输入） | BOOL | [5 empty] | X
控制命令 | 7 | 2 | 400008 | 03; 06; 16 | 外部电压控制（接收外部电压或其它信号输入） | BOOL | [5 empty] | X
控制命令 | 7 | 3 | 400008 | 03; 06; 16 | 外部有功控制（接收外部电压或其它信号输入） | BOOL |  |  |  |  | X | X
控制命令 | 7 | 4 | 400008 | 03; 06; 16 | 外部无功控制（接收外部电压或其它信号输入） | BOOL | [5 empty] | X
控制命令 | 7 | 5 | 400008 | 03; 06; 16 | 外部功率因素控制（接收外部电压或其它信号输入） | BOOL | [5 empty] | X
控制命令 | 7 | 6 | 400008 | 03; 06; 16 | 容性功率因数 | BOOL | [5 empty] | X
控制命令 | 7 | 7 | 400008 | 03; 06; 16 | 基本负载（Base load） | BOOL | [5 empty] | X
控制命令 | 7 | 8 | 400008 | 03; 06; 16 | 第一优先级选择 | BOOL | [5 empty] | X
控制命令 | 7 | 9 | 400008 | 03; 06; 16 | 应用1选择 | BOOL |  |  |  | X | X | X
控制命令 | 7 | 10 | 400008 | 03; 06; 16 | 应用2选择 | BOOL |  |  |  | X | X | X
控制命令 | 7 | 11 | 400008 | 03; 06; 16 | 应用3选择 | BOOL |  |  |  | X | X | X
控制命令 | 7 | 12 | 400008 | 03; 06; 16 | 应用4选择 | BOOL |  |  |  | X | X | X
控制命令 | 7 | 13 | 400008 | 03; 06; 16 | 电池测试激活 | BOOL | [5 empty] | X
控制命令 | 7 | 15 | 400008 | 03; 06; 16 | 同步时钟到 4:00 a.m. | BOOL |  |  |  | X | X | X
控制命令 | 8 | 0 | 400009 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 8 | 1 | 400009 | 03; 06; 16 | 虚拟事件激活 1 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 2 | 400009 | 03; 06; 16 | 虚拟事件2脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 3 | 400009 | 03; 06; 16 | 虚拟事件激活 3 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 4 | 400009 | 03; 06; 16 | 虚拟事件激活 4 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 5 | 400009 | 03; 06; 16 | 虚拟事件5脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 6 | 400009 | 03; 06; 16 | 虚拟事件6脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 7 | 400009 | 03; 06; 16 | 虚拟事件7脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 8 | 400009 | 03; 06; 16 | 虚拟事件8脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 9 | 400009 | 03; 06; 16 | 虚拟事件9脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 10 | 400009 | 03; 06; 16 | 虚拟事件10脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 11 | 400009 | 03; 06; 16 | 虚拟事件11脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 12 | 400009 | 03; 06; 16 | 虚拟事件12脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 13 | 400009 | 03; 06; 16 | 虚拟事件13脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 14 | 400009 | 03; 06; 16 | 虚拟事件14脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 8 | 15 | 400009 | 03; 06; 16 | 虚拟事件15脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 0 | 400010 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 9 | 1 | 400010 | 03; 06; 16 | 虚拟事件16脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 2 | 400010 | 03; 06; 16 | 虚拟事件17脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 3 | 400010 | 03; 06; 16 | 虚拟事件18脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 4 | 400010 | 03; 06; 16 | 虚拟事件19脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 5 | 400010 | 03; 06; 16 | 虚拟事件20脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 6 | 400010 | 03; 06; 16 | 虚拟事件21脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 7 | 400010 | 03; 06; 16 | 虚拟事件22脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 8 | 400010 | 03; 06; 16 | 虚拟事件23脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 9 | 400010 | 03; 06; 16 | 虚拟事件24脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 10 | 400010 | 03; 06; 16 | 虚拟事件25脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 11 | 400010 | 03; 06; 16 | 虚拟事件26脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 12 | 400010 | 03; 06; 16 | 虚拟事件27脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 13 | 400010 | 03; 06; 16 | 虚拟事件28脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 14 | 400010 | 03; 06; 16 | 虚拟事件29脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 9 | 15 | 400010 | 03; 06; 16 | 虚拟事件30脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 10 | 0 | 400011 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 10 | 1 | 400011 | 03; 06; 16 | 虚拟事件31脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 10 | 2 | 400011 | 03; 06; 16 | 虚拟事件32脉冲激活 | BOOL |  |  |  | X | X | X
控制命令 | 10 | 4 | 400011 | 03; 06; 16 | 清除历史记录 | BOOL |  |  |  | X | X | X
控制命令 | 10 | 5 | 400011 | 03; 06; 16 | 清除参数编辑（带笔的标志） | BOOL |  |  |  | X | X | X
控制命令 | 13 | 0 | 400014 | 03; 06; 16 | 当写这控制字节时这位必须为1.如果这位为0, 这控制命令无效. | BOOL |  |  |  | X | X | X
控制命令 | 13 | 1 | 400014 | 03; 06; 16 | 使能外部频率控制 | BOOL | [5 empty] | X
控制命令 | 13 | 2 | 400014 | 03; 06; 16 | 不使能外部频率控制 | BOOL | [5 empty] | X
控制命令 | 13 | 3 | 400014 | 03; 06; 16 | 使能外部电压控制 | BOOL | [5 empty] | X
控制命令 | 13 | 4 | 400014 | 03; 06; 16 | 不使能外部电压控制 | BOOL | [5 empty] | X
控制命令 | 13 | 5 | 400014 | 03; 06; 16 | 使能外部有功控制 | BOOL |  |  |  |  | X | X
控制命令 | 13 | 6 | 400014 | 03; 06; 16 | 不使能外部有功控制 | BOOL |  |  |  |  | X | X
控制命令 | 13 | 7 | 400014 | 03; 06; 16 | 使能外部无功控制 | BOOL | [5 empty] | X
控制命令 | 13 | 8 | 400014 | 03; 06; 16 | 不使能外部无功控制 | BOOL | [5 empty] | X
控制命令 | 13 | 9 | 400014 | 03; 06; 16 | 使能外部功率因数控制 | BOOL | [5 empty] | X
控制命令 | 13 | 10 | 400014 | 03; 06; 16 | 不使能外部功率因数控制 | BOOL | [5 empty] | X
控制命令 | 13 | 11 | 400014 | 03; 06; 16 | 使能PM基本负载（base load）控制 | BOOL | [5 empty] | X
控制命令 | 13 | 12 | 400014 | 03; 06; 16 | 不使能PM基本负载（base load）控制 | BOOL | [5 empty] | X
控制命令 | 13 | 13 | 400014 | 03; 06; 16 | 消音 | BOOL |  |  |  | X | X | X
控制时间命令 | 58000 |  | 458001 | 03; 06; 16 | 年（2003-2099） | INT16s | AB | 0 |  | X | X | X
控制时间命令 | 58001 |  | 458002 | 03; 06; 16 | 月（1-12） | INT16s | AB | 0 |  | X | X | X
控制时间命令 | 58002 |  | 458003 | 03; 06; 16 | 日（1-31） | INT16s | AB | 0 |  | X | X | X
控制时间命令 | 58003 |  | 458004 | 03; 06; 16 | 星期（1-7，Monday - Sunday） | INT16s | AB | 0 |  | X | X | X
控制时间命令 | 58004 |  | 458005 | 03; 06; 16 | 时 (0-23) | INT16s | AB | 0 |  | X | X | X
控制时间命令 | 58005 |  | 458006 | 03; 06; 16 | 分 (0-59) | INT16s | AB | 0 |  | X | X | X
控制时间命令 | 58006 |  | 458007 | 03; 06; 16 | 秒 (0-59) | INT16s | AB | 0 |  | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on C4: Bit location of the function in the associated Modbus address.
Note on E4: 03 - Read single or multiple 06 - Write single 16 - Write multiple
Note on F4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on H4: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I4: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on J4: Unit of the associated function
Note on K4: Indicates if the address is available in the BUS TIE breaker controller.
Note on L4: Indicates if the address is available in the MAINS controller.
Note on M4: Indicates if the address is available in the GENSET controller.

## Input register (04)
输入寄存器 (04)
功能组 | Modbus 地址 | 位 | PLC地址 | Modbus 功能码 | 通道号 | 注解 | 数据类型 | 数据格式 | 比例 (10⁻ˣ) | 单位 | BTB单元 | 主网单元 | 机组单元
AC 测量 | 500 |  | 300501 | 4 |  | 应用版本 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 501 |  | 300502 | 4 |  | 发电机电压L1-L2 | INT16s | AB | 0 | V |  |  | X
AC 测量 | 501 |  | 300502 | 4 |  | 母排A 电压 L1-L2 | INT16s | AB | 0 | V | X
AC 测量 | 501 |  | 300502 | 4 |  | 主网(市电) 电压 L1-L2 | INT16s | AB | 0 | V |  | X
AC 测量 | 502 |  | 300503 | 4 |  | 母排 A 电压 L2-L3 | INT16s | AB | 0 | V | X
AC 测量 | 502 |  | 300503 | 4 |  | 发电机电压 L2-L3 | INT16s | AB | 0 | V |  |  | X
AC 测量 | 502 |  | 300503 | 4 |  | 主网(市电) 电压 L2-L3 | INT16s | AB | 0 | V |  | X
AC 测量 | 503 |  | 300504 | 4 |  | 发电机电压L3-L1 | INT16s | AB | 0 | V |  |  | X
AC 测量 | 503 |  | 300504 | 4 |  | 母排 B 电压 L3-L1 | INT16s | AB | 0 | V |  | X
AC 测量 | 503 |  | 300504 | 4 |  | 母排 A 电压 L3-L1 | INT16s | AB | 0 | V | X
AC 测量 | 504 |  | 300505 | 4 |  | 发电机电压L1-N | INT16s | AB | 0 | V |  |  | X
AC 测量 | 504 |  | 300505 | 4 |  | 母排 A 电压 L1-N | INT16s | AB | 0 | V | X
AC 测量 | 504 |  | 300505 | 4 |  | 主网(市电) 电压 L1-N | INT16s | AB | 0 | V |  | X
AC 测量 | 505 |  | 300506 | 4 |  | 发电机电压L2-N | INT16s | AB | 0 | V |  |  | X
AC 测量 | 505 |  | 300506 | 4 |  | 母排 A 电压 L2-N | INT16s | AB | 0 | V | X
AC 测量 | 505 |  | 300506 | 4 |  | 主网(市电) 电压 L2-N | INT16s | AB | 0 | V |  | X
AC 测量 | 506 |  | 300507 | 4 |  | 发电机电压L3-N | INT16s | AB | 0 | V |  |  | X
AC 测量 | 506 |  | 300507 | 4 |  | 母排 A 电压 L3-N | INT16s | AB | 0 | V | X
AC 测量 | 506 |  | 300507 | 4 |  | 主网(市电) 电压 L3-N | INT16s | AB | 0 | V |  | X
AC 测量 | 507 |  | 300508 | 4 |  | 发电机频率 L1 | INT16s | AB | 2 | Hz |  |  | X
AC 测量 | 507 |  | 300508 | 4 |  | 母排 A频率 L1 | INT16s | AB | 2 | Hz | X
AC 测量 | 507 |  | 300508 | 4 |  | 主网（市电）频率 L1 | INT16s | AB | 2 | Hz |  | X
AC 测量 | 508 |  | 300509 | 4 |  | 发电机频率 L2 | INT16s | AB | 2 | Hz |  |  | X
AC 测量 | 508 |  | 300509 | 4 |  | 主网（市电）频率 L2 | INT16s | AB | 2 | Hz |  | X
AC 测量 | 508 |  | 300509 | 4 |  | 母排 A频率 L2 | INT16s | AB | 2 | Hz | X
AC 测量 | 509 |  | 300510 | 4 |  | 发电机频率 L3 | INT16s | AB | 2 | Hz |  |  | X
AC 测量 | 509 |  | 300510 | 4 |  | 母排A 频率 L3 | INT16s | AB | 2 | Hz | X
AC 测量 | 509 |  | 300510 | 4 |  | 主网（市电）频率 L3 | INT16s | AB | 2 | Hz |  | X
AC 测量 | 510 |  | 300511 | 4 |  | 母排A 电压 相角 L1-L2 | INT16s | AB | 1 | 度 | X
AC 测量 | 510 |  | 300511 | 4 |  | 发电机电压 相角 L1-L2 | INT16s | AB | 1 | 度 |  |  | X
AC 测量 | 510 |  | 300511 | 4 |  | 主网(市电) 电压 相角 L1-L2 | INT16s | AB | 1 | 度 |  | X
AC 测量 | 511 |  | 300512 | 4 |  | 发电机电压相角L2-L3 | INT16s | AB | 1 | 度 |  |  | X
AC 测量 | 511 |  | 300512 | 4 |  | 主网(市电) 电压相角L2-L3 | INT16s | AB | 1 | 度 |  | X
AC 测量 | 511 |  | 300512 | 4 |  | 母排 A 电压相角L2-L3 | INT16s | AB | 1 | 度 | X
AC 测量 | 512 |  | 300513 | 4 |  | 母排 A 电压相角L3-L1 | INT16s | AB | 1 | 度 | X
AC 测量 | 512 |  | 300513 | 4 |  | 发电机电压相角L3-L1 | INT16s | AB | 1 | 度 |  |  | X
AC 测量 | 512 |  | 300513 | 4 |  | 电源电压的相角L3-L1 | INT16s | AB | 1 | 度 |  | X
AC 测量 | 513 |  | 300514 | 4 |  | 发电机电流 L1 | INT16s | AB | 0 | A |  |  | X
AC 测量 | 513 |  | 300514 | 4 |  | 主网(市电) 电流 L1 | INT16s | AB | 0 | A |  | X
AC 测量 | 513 |  | 300514 | 4 |  | 母排 A 电流 L1 | INT16s | AB | 0 | A | X
AC 测量 | 514 |  | 300515 | 4 |  | 发电机电流 L2 | INT16s | AB | 0 | A |  |  | X
AC 测量 | 514 |  | 300515 | 4 |  | 母排 A 电流 L2 | INT16s | AB | 0 | A | X
AC 测量 | 514 |  | 300515 | 4 |  | 主网(市电) 电流 L2 | INT16s | AB | 0 | A |  | X
AC 测量 | 515 |  | 300516 | 4 |  | 发电机电流 L3 | INT16s | AB | 0 | A |  |  | X
AC 测量 | 515 |  | 300516 | 4 |  | 母排 A 电流 L3 | INT16s | AB | 0 | A | X
AC 测量 | 515 |  | 300516 | 4 |  | 主网(市电) 电流 L3 | INT16s | AB | 0 | A |  | X
AC 测量 | 516 |  | 300517 | 4 |  | 母排A 功率 L1 | INT16s | AB | 0 | kW | X
AC 测量 | 516 |  | 300517 | 4 |  | 发电机功率 L1 | INT16s | AB | 0 | kW |  |  | X
AC 测量 | 516 |  | 300517 | 4 |  | 主网(市电) 功率L1 | INT16s | AB | 0 | kW |  | X
AC 测量 | 517 |  | 300518 | 4 |  | 发电机功率 L2 | INT16s | AB | 0 | kW |  |  | X
AC 测量 | 517 |  | 300518 | 4 |  | 母排 A 功率 L2 | INT16s | AB | 0 | kW | X
AC 测量 | 517 |  | 300518 | 4 |  | 主网(市电) 功率L2 | INT16s | AB | 0 | kW |  | X
AC 测量 | 518 |  | 300519 | 4 |  | 母排A 功率 L3 | INT16s | AB | 0 | kW | X
AC 测量 | 518 |  | 300519 | 4 |  | 发电机功率 L3 | INT16s | AB | 0 | kW |  |  | X
AC 测量 | 518 |  | 300519 | 4 |  | 主网(市电) 功率L3 | INT16s | AB | 0 | kW |  | X
AC 测量 | 519 |  | 300520 | 4 |  | 发电机功率 | INT16s | AB | 0 | kW |  |  | X
AC 测量 | 519 |  | 300520 | 4 |  | 母排 A 功率 | INT16s | AB | 0 | kW | X
AC 测量 | 519 |  | 300520 | 4 |  | 主电网功率 | INT16s | AB | 0 | kW |  | X
AC 测量 | 520 |  | 300521 | 4 |  | 发电机无功功率 L1 | INT16s | AB | 0 | kVAr |  |  | X
AC 测量 | 520 |  | 300521 | 4 |  | 母排A 无功功率 L1 | INT16s | AB | 0 | kVAr | X
AC 测量 | 520 |  | 300521 | 4 |  | 主网(市电) 无功功率 L1 | INT16s | AB | 0 | kVAr |  | X
AC 测量 | 521 |  | 300522 | 4 |  | 发电机无功功率 L2 | INT16s | AB | 0 | kVAr |  |  | X
AC 测量 | 521 |  | 300522 | 4 |  | 主网(市电) 无功功率 L2 | INT16s | AB | 0 | kVAr |  | X
AC 测量 | 521 |  | 300522 | 4 |  | 母排A 无功功率 L2 | INT16s | AB | 0 | kVAr | X
AC 测量 | 522 |  | 300523 | 4 |  | 发电机 无功功率 L3 | INT16s | AB | 0 | kVAr |  |  | X
AC 测量 | 522 |  | 300523 | 4 |  | 母排A 无功功率 L3 | INT16s | AB | 0 | kVAr | X
AC 测量 | 522 |  | 300523 | 4 |  | 主网(市电) 无功功率 L3 | INT16s | AB | 0 | kVAr |  | X
AC 测量 | 523 |  | 300524 | 4 |  | 发电机 无功功率 | INT16s | AB | 0 | kVAr |  |  | X
AC 测量 | 523 |  | 300524 | 4 |  | 母排A 无功功率 | INT16s | AB | 0 | kVAr | X
AC 测量 | 523 |  | 300524 | 4 |  | 主网(市电) 无功功率 | INT16s | AB | 0 | kVAr |  | X
AC 测量 | 524 |  | 300525 | 4 |  | 发电机视在功率，L1 | INT16s | AB | 0 | kVA |  |  | X
AC 测量 | 524 |  | 300525 | 4 |  | 母排A视在功率L1 | INT16s | AB | 0 | kVA | X
AC 测量 | 524 |  | 300525 | 4 |  | 主网(市电) 视在功率 L1 | INT16s | AB | 0 | kVA |  | X
AC 测量 | 525 |  | 300526 | 4 |  | 发电机视在功率，L2 | INT16s | AB | 0 | kVA |  |  | X
AC 测量 | 525 |  | 300526 | 4 |  | 母排A视在功率L2 | INT16s | AB | 0 | kVA | X
AC 测量 | 525 |  | 300526 | 4 |  | 主网(市电) 视在功率 L2 | INT16s | AB | 0 | kVA |  | X
AC 测量 | 526 |  | 300527 | 4 |  | 发电机视在功率，L3 | INT16s | AB | 0 | kVA |  |  | X
AC 测量 | 526 |  | 300527 | 4 |  | 母排A视在功率L3 | INT16s | AB | 0 | kVA | X
AC 测量 | 526 |  | 300527 | 4 |  | 主网(市电) 视在功率 L3 | INT16s | AB | 0 | kVA |  | X
AC 测量 | 527 |  | 300528 | 4 |  | 发电机视在功率 | INT16s | AB | 0 | kVA |  |  | X
AC 测量 | 527 |  | 300528 | 4 |  | 母排A视在功率 | INT16s | AB | 0 | kVA | X
AC 测量 | 527 |  | 300528 | 4 |  | 主网(市电) 视在功率 | INT16s | AB | 0 | kVA |  | X
AC 测量 | 528 |  | 300529 | 4 |  | 发电机 输出无功电能计数 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 528 |  | 300529 | 4 |  | 母排A 输出无功电能计数, | INT32s | A B C D | 0 | kVArh | X
AC 测量 | 528 |  | 300529 | 4 |  | 主网(市电) 输出无功电能计数 | INT32s | A B C D | 0 | kVArh |  | X
AC 测量 | 530 |  | 300531 | 4 |  | 母排A 输出, 有功电能计数, 天 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 530 |  | 300531 | 4 |  | 发电机 输出, 有功电能计数, 天 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 530 |  | 300531 | 4 |  | 主网(市电) 输出, 有功电能计数, 天 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 532 |  | 300533 | 4 |  | 母排A 输出, 有功电能计数，周 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 532 |  | 300533 | 4 |  | 发电机 输出, 有功电能计数, 周 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 532 |  | 300533 | 4 |  | 主网(市电) 输出, 有功电能计数, 周 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 534 |  | 300535 | 4 |  | 发电机 输出, 有功电能计数, 月 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 534 |  | 300535 | 4 |  | 母排A 输出, 有功电能计数，月 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 534 |  | 300535 | 4 |  | 主网(市电) 输出, 有功电能计数, 月 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 536 |  | 300537 | 4 |  | 发电机 输出, 有功电能计数, 总计 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 536 |  | 300537 | 4 |  | 母排A 输出, 有功电能计数，总计 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 536 |  | 300537 | 4 |  | 主网(市电) 输出, 有功电能计数, 总计 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 538 |  | 300539 | 4 |  | 发电机PF | INT16s | AB | 2 | PF |  |  | X
AC 测量 | 538 |  | 300539 | 4 |  | 母排A PF | INT16s | AB | 2 | PF | X
AC 测量 | 538 |  | 300539 | 4 |  | 主网(市电) PF | INT16s | AB | 2 | PF |  | X
AC 测量 | 539 |  | 300540 | 4 |  | 母排电压 L1-L2 | INT16s | AB | 0 | V | X | X | X
AC 测量 | 540 |  | 300541 | 4 |  | 母排电压 L2-L3 | INT16s | AB | 0 | V | X | X | X
AC 测量 | 541 |  | 300542 | 4 |  | 母排电压 L3-L1 | INT16s | AB | 0 | V | X | X | X
AC 测量 | 542 |  | 300543 | 4 |  | 母排电压 L1-N | INT16s | AB | 0 | V | X | X | X
AC 测量 | 543 |  | 300544 | 4 |  | 母排电压 L2-N | INT16s | AB | 0 | V | X | X | X
AC 测量 | 544 |  | 300545 | 4 |  | 总线 B 电压 L3-N | INT16s | AB | 0 | V | X | X | X
AC 测量 | 545 |  | 300546 | 4 |  | 母排频率 L1 | INT16s | AB | 2 | Hz | X | X | X
AC 测量 | 546 |  | 300547 | 4 |  | 母排频率 L2 | INT16s | AB | 2 | Hz | X | X | X
AC 测量 | 547 |  | 300548 | 4 |  | 母排频率 L3 | INT16s | AB | 2 | Hz | X | X | X
AC 测量 | 548 |  | 300549 | 4 |  | 母排电压 相角 L1-L2 | INT16s | AB | 1 | 度 | X | X | X
AC 测量 | 549 |  | 300550 | 4 |  | 母排电压 相角 L2-L3 | INT16s | AB | 1 | 度 | X | X | X
AC 测量 | 550 |  | 300551 | 4 |  | 母排电压 相角 L3-L1 | INT16s | AB | 1 | 度 | X | X | X
AC 测量 | 551 |  | 300552 | 4 |  | U BB L1 - U DG L1 相角 | INT16s | AB | 1 | 度 |  |  | X
AC 测量 | 551 |  | 300552 | 4 |  | U BB A L1 - U BB B L1 相角 | INT16s | AB | 1 | 度 | X
AC 测量 | 551 |  | 300552 | 4 |  | U BB L1 - U Mains L1 相角 | INT16s | AB | 1 | 度 |  | X
AC 测量 | 552 |  | 300553 | 4 |  | U BB L2 - U GEN L2 相角 | INT16s | AB | 1 | 度 |  |  | X
AC 测量 | 552 |  | 300553 | 4 |  | U BB A L2 - U BB B L2 相角 | INT16s | AB | 1 | 度 | X
AC 测量 | 552 |  | 300553 | 4 |  | U BB L2 - U Mains L2 相角 | INT16s | AB | 1 | 度 |  | X
AC 测量 | 553 |  | 300554 | 4 |  | U BB L3 - U GEN L3 相角 | INT16s | AB | 1 | 度 |  |  | X
AC 测量 | 553 |  | 300554 | 4 |  | U BB A L3 - U BB B L3相角 | INT16s | AB | 1 | 度 | X
AC 测量 | 553 |  | 300554 | 4 |  | U BB L3 - U Mains L3 相角 | INT16s | AB | 1 | 度 |  | X
AC 测量 | 554 |  | 300555 | 4 |  | 绝对运行小时 | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 556 |  | 300557 | 4 |  | 相对运行小时 | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 558 |  | 300559 | 4 |  | 报警数 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 559 |  | 300560 | 4 |  | 未确认的报警数 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 560 |  | 300561 | 4 |  | 已确认的报警数 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 561 |  | 300562 | 4 |  | 运行分钟计数，停机忽略 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 562 |  | 300563 | 4 |  | 运行小时计数，停机忽略 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 563 |  | 300564 | 4 |  | GB合闸次数 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 563 |  | 300564 | 4 |  | BTB合闸次数 | INT16s | AB | 0 |  | X
AC 测量 | 563 |  | 300564 | 4 |  | TB合闸次数 | INT16s | AB | 0 |  |  | X
AC 测量 | 564 |  | 300565 | 4 |  | MB 合闸次数 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 566 |  | 300567 | 4 |  | 启动次数 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 567 |  | 300568 | 4 |  | DC电压（模块端子1-2之间） | INT16s | AB | 1 | V | X | X | X
AC 测量 | 569 |  | 300570 | 4 |  | 保养周期1 运行小时 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 570 |  | 300571 | 4 |  | 保养周期1 运行天数 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 571 |  | 300572 | 4 |  | 保养周期 2 运行小时 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 572 |  | 300573 | 4 |  | 保养周期 2 运行天数 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 573 |  | 300574 | 4 |  | 功率因数 | INT16s | AB | 2 | cosPhi | X | X | X
AC 测量 | 574 |  | 300575 | 4 |  | 功率因数 感性/容性 0 = 感性，1 = 容性 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 576 |  | 300577 | 4 |  | 转速 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 577 |  | 300578 | 4 |  | 运行小时负载曲线%（load profile） | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 583 |  | 300584 | 4 |  | 多功能输入 46 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 584 |  | 300585 | 4 |  | 多功能输入 47 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 585 |  | 300586 | 4 |  | 多功能输入 48 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 591 |  | 300592 | 4 |  | 母排功率，多功能输入 47 | INT16s | AB | 0 | kW |  | X
AC 测量 | 591 |  | 300592 | 4 |  | 母排A功率, 多功能输入47 | INT16s | AB | 0 | kW | X
AC 测量 | 592 |  | 300593 | 4 |  | 主网(市电) 功率, 多功能输入 46 | INT16s | AB | 0 | kW |  | X | X
AC 测量 | 593 |  | 300594 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 594 |  | 300595 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 595 |  | 300596 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 596 |  | 300597 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 597 |  | 300598 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 598 |  | 300599 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 599 |  | 300600 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 600 |  | 300601 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 601 |  | 300602 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 602 |  | 300603 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 603 |  | 300604 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 604 |  | 300605 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 605 |  | 300606 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 606 |  | 300607 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 607 |  | 300608 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 608 |  | 300609 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 609 |  | 300610 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 610 |  | 300611 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 611 |  | 300612 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 612 |  | 300613 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 613 |  | 300614 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 614 |  | 300615 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 615 |  | 300616 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 616 |  | 300617 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 617 |  | 300618 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 618 |  | 300619 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 619 |  | 300620 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 620 |  | 300621 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 621 |  | 300622 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 622 |  | 300623 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 623 |  | 300624 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 624 |  | 300625 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 625 |  | 300626 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 626 |  | 300627 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 627 |  | 300628 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 628 |  | 300629 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 629 |  | 300630 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 630 |  | 300631 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 631 |  | 300632 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 632 |  | 300633 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 633 |  | 300634 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 634 |  | 300635 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 635 |  | 300636 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 636 |  | 300637 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 637 |  | 300638 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 638 |  | 300639 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 639 |  | 300640 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 640 |  | 300641 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 641 |  | 300642 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 642 |  | 300643 | 4 |  | 控制寄存器地址 0 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 643 |  | 300644 | 4 |  | 控制寄存器地址 1 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 644 |  | 300645 | 4 |  | 控制寄存器地址 2 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 645 |  | 300646 | 4 |  | 控制寄存器地址 3 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 646 |  | 300647 | 4 |  | 控制寄存器地址 4 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 647 |  | 300648 | 4 |  | 控制寄存器地址 5 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 648 |  | 300649 | 4 |  | 控制寄存器地址 6 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 649 |  | 300650 | 4 |  | 控制寄存器地址 7 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 650 |  | 300651 | 4 |  | 控制寄存器地址 8 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 651 |  | 300652 | 4 |  | 控制寄存器地址 9 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 652 |  | 300653 | 4 |  | 控制寄存器地址 10 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 653 |  | 300654 | 4 |  | 控制寄存器地址 11 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 654 |  | 300655 | 4 |  | 控制寄存器地址 12 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 655 |  | 300656 | 4 |  | 控制寄存器地址 13 | INT16s | AB | 0 |  | X | X | X
AC 测量 | 660 |  | 300661 | 4 |  | 扩展模拟量 1/CIO 308 no. 1.输入点8 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 661 |  | 300662 | 4 |  | 扩展模拟量 2/CIO 308 no. 1.输入点11 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 662 |  | 300663 | 4 |  | 扩展模拟量 3/CIO 308 no. 1.输入点14 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 663 |  | 300664 | 4 |  | 扩展模拟量 4/CIO 308 no. 1.输入点17 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 664 |  | 300665 | 4 |  | 扩展模拟量 5/CIO 308 no. 1.输入点20 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 665 |  | 300666 | 4 |  | 扩展模拟量 6/CIO 308 no. 1.输入点23 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 666 |  | 300667 | 4 |  | 扩展模拟量 7/CIO 308 no. 1.输入点26 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 667 |  | 300668 | 4 |  | 扩展模拟量 8/CIO 308 no. 1.输入点29 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 668 |  | 300669 | 4 |  | CIO 308 no. 2.输入点8 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 669 |  | 300670 | 4 |  | CIO 308 no. 2.输入点11 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 670 |  | 300671 | 4 |  | CIO 308 no. 2.输入点14 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 671 |  | 300672 | 4 |  | CIO 308 no. 2.输入点17 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 672 |  | 300673 | 4 |  | CIO 308 no. 2.输入点20 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 673 |  | 300674 | 4 |  | CIO 308 no. 2.输入点23 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 674 |  | 300675 | 4 |  | CIO 308 no. 2.输入点26 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 675 |  | 300676 | 4 |  | CIO 308 no. 2.输入点29 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 676 |  | 300677 | 4 |  | CIO 308 no. 3.输入点8 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 677 |  | 300678 | 4 |  | CIO 308 no. 3.输入点11 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 678 |  | 300679 | 4 |  | CIO 308 no. 3.输入点14 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 679 |  | 300680 | 4 |  | CIO 308 no. 3.输入点17 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 680 |  | 300681 | 4 |  | CIO 308 no. 3.输入点20 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 681 |  | 300682 | 4 |  | CIO 308 no. 3.输入点23 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 682 |  | 300683 | 4 |  | CIO 308 no. 3.输入点26 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 683 |  | 300684 | 4 |  | CIO 308 no. 3.输入点29 [可配置] | INT16s | AB | 0 |  | X | X | X
AC 测量 | 696 |  | 300697 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 697 |  | 300698 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 698 |  | 300699 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 699 |  | 300700 | 4 |  | 见 设计参考手册 | INT16s | AB | 0 |  |  |  | X
AC 测量 | 700 |  | 300701 | 4 |  | 实际额定功率 (包含折损等.) | INT16s | AB | 0 |  | X | X | X
AC 测量 | 701 |  | 300702 | 4 |  | 主网(市电) 功率变送器（变送器被使用） | INT16s | AB | 0 |  |  | X | X
AC 测量 | 702 |  | 300703 | 4 |  | 风扇 A 运行小时 | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 704 |  | 300705 | 4 |  | 风扇 B 运行小时 | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 706 |  | 300707 | 4 |  | 风扇 C 运行小时 | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 708 |  | 300709 | 4 |  | 风扇 D 运行小时 | INT32s | A B C D | 0 |  |  |  | X
AC 测量 | 790 |  | 300791 | 4 |  | 发电机 输出无功电能计数, 月 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 790 |  | 300791 | 4 |  | 母排A 输出无功电能计数, 月 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 790 |  | 300791 | 4 |  | 主网(市电) 输出无功电能计数,月 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 792 |  | 300793 | 4 |  | 发电机 输出无功电能计数，周 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 792 |  | 300793 | 4 |  | 母排A 输出无功电能计数，周 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 792 |  | 300793 | 4 |  | 主网(市电) 输出无功电能计数,周 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 794 |  | 300795 | 4 |  | 母排A 输出无功电能计数, 总计 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 794 |  | 300795 | 4 |  | 发电机 输出无功电能计数, 总计 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 794 |  | 300795 | 4 |  | 主网(市电) 输出无功电能计数，总计 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 796 |  | 300797 | 4 |  | 母排A 输入有功电能计数, 总计 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 796 |  | 300797 | 4 |  | 发电机 输入有功电能计数, 总计 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 796 |  | 300797 | 4 |  | 主网(市电) 输入有功电能计数, 总计 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 798 |  | 300799 | 4 |  | 发电机 输入有功电能计数, 月 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 798 |  | 300799 | 4 |  | 母排A 输入有功电能计数, 月 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 798 |  | 300799 | 4 |  | 主网(市电) 输入有功电能计数, 月 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 800 |  | 300801 | 4 |  | 发电机 输入有功电能计数, 周 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 800 |  | 300801 | 4 |  | 主网(市电) 输入有功电能计数, 周 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 800 |  | 300801 | 4 |  | 母排A 输入有功电能计数, 周 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 802 |  | 300803 | 4 |  | 母排A 输入有功电能计数, 天 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 802 |  | 300803 | 4 |  | 发电机 输入有功电能计数, 天 | INT32s | A B C D | 0 | kWh |  |  | X
AC 测量 | 802 |  | 300803 | 4 |  | 主网(市电) 输入有功电能计数, 天 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 804 |  | 300805 | 4 |  | 发电机 输入无功电能计数, 总计 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 804 |  | 300805 | 4 |  | 母排A 输入无功电能计数, 总计 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 804 |  | 300805 | 4 |  | 主网(市电) 输入无功电能计数, 总计 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 806 |  | 300807 | 4 |  | 发电机 输入无功电能计数, 月 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 806 |  | 300807 | 4 |  | 母排A 输入无功电能计数, 月 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 806 |  | 300807 | 4 |  | 主网(市电) 输入无功电能计数, 月 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 808 |  | 300809 | 4 |  | 母排A 输入无功电能计数, 周 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 808 |  | 300809 | 4 |  | 发电机 输入无功电能计数, 周 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 808 |  | 300809 | 4 |  | 主网(市电) 输入无功电能计数, 周 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 810 |  | 300811 | 4 |  | 发电机 输入无功电能计数, 天 | INT32s | A B C D | 0 | kVArh |  |  | X
AC 测量 | 810 |  | 300811 | 4 |  | 母排A 输入无功电能计数, 天 | INT32s | A B C D | 0 | kWh | X
AC 测量 | 810 |  | 300811 | 4 |  | 主网(市电) 输入无功电能计数, 天 | INT32s | A B C D | 0 | kWh |  | X
AC 测量 | 812 |  | 300813 | 4 |  | 脉冲计数 01 | INT32s | A B C D | 0 |  | X | X | X
AC 测量 | 814 |  | 300815 | 4 |  | 脉冲计数 02 | INT32s | A B C D | 0 |  | X | X | X
AC 测量 | 816 |  | 300817 | 4 |  | 峰值电流需求值 1 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 817 |  | 300818 | 4 |  | 峰值电流需求值 2 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 818 |  | 300819 | 4 |  | 峰值电流需求值 3 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 819 |  | 300820 | 4 |  | 峰值平均电流需求值 1 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 820 |  | 300821 | 4 |  | 峰值平均电流需求值 2 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 821 |  | 300822 | 4 |  | 峰值平均电流需求值 3 | INT16s | AB | 0 |  |  | X | X
AC 测量 | 822 |  | 300823 | 4 |  | 起动次数（标准） | INT16s | AB | 0 |  |  |  | X
AC 测量 | 823 |  | 300824 | 4 |  | 起动次数（双起动马达） | INT16s | AB | 0 |  |  |  | X
报警 | 1000 | 0 | 301001 | 4 | 1000 | 机组逆功 1 | BOOL | [5 empty] | X
报警 | 1000 | 0 | 301001 | 4 | 1000 | 母排A逆功 1 | BOOL |  |  |  | X
报警 | 1000 | 0 | 301001 | 4 | 1000 | 主网(市电)逆功 1 | BOOL |  |  |  |  | X
报警 | 1000 | 1 | 301001 | 4 | 1010 | 机组逆功 2 | BOOL | [5 empty] | X
报警 | 1000 | 1 | 301001 | 4 | 1010 | 母排A逆功 2 | BOOL |  |  |  | X
报警 | 1000 | 1 | 301001 | 4 | 1010 | 主网(市电)逆功 2 | BOOL |  |  |  |  | X
报警 | 1000 | 3 | 301001 | 4 | 1030 | 机组过电流 1 | BOOL | [5 empty] | X
报警 | 1000 | 3 | 301001 | 4 | 1030 | 母排A过电流 1 | BOOL |  |  |  | X
报警 | 1000 | 3 | 301001 | 4 | 1030 | 主网(市电)过电流 1 | BOOL |  |  |  |  | X
报警 | 1000 | 4 | 301001 | 4 | 1040 | 机组过电流 2 | BOOL | [5 empty] | X
报警 | 1000 | 4 | 301001 | 4 | 1040 | 母排A过电流 2 | BOOL |  |  |  | X
报警 | 1000 | 4 | 301001 | 4 | 1040 | 主网(市电)过电流 2 | BOOL |  |  |  |  | X
报警 | 1000 | 5 | 301001 | 4 | 1050 | 机组过电流 3 | BOOL | [5 empty] | X
报警 | 1000 | 5 | 301001 | 4 | 1050 | 母排A过电流 3 | BOOL |  |  |  | X
报警 | 1000 | 5 | 301001 | 4 | 1050 | 主网(市电)过电流 3 | BOOL |  |  |  |  | X
报警 | 1000 | 6 | 301001 | 4 | 1060 | 机组过电流 4 | BOOL | [5 empty] | X
报警 | 1000 | 6 | 301001 | 4 | 1060 | 母排A过电流 4 | BOOL |  |  |  | X
报警 | 1000 | 6 | 301001 | 4 | 1060 | 主网(市电)过电流 4 | BOOL |  |  |  |  | X
报警 | 1000 | 7 | 301001 | 4 | 1087 | 机组反时限过电流 | BOOL | [5 empty] | X
报警 | 1000 | 7 | 301001 | 4 | 1087 | 母排A反时限过电流 | BOOL |  |  |  | X
报警 | 1000 | 7 | 301001 | 4 | 1087 | 主网(市电)反时限过电流 | BOOL |  |  |  |  | X
报警 | 1000 | 8 | 301001 | 4 | 1110 | 机组低电压过电流 | BOOL |  |  |  | X | X | X
报警 | 1000 | 9 | 301001 | 4 | 1130 | 机组过电流 1 | BOOL | [5 empty] | X
报警 | 1000 | 9 | 301001 | 4 | 1130 | 母排A过电流 1 | BOOL |  |  |  | X
报警 | 1000 | 9 | 301001 | 4 | 1130 | 主网(市电)过电流 1 | BOOL |  |  |  |  | X
报警 | 1000 | 10 | 301001 | 4 | 1140 | 机组过电流 2 | BOOL | [5 empty] | X
报警 | 1000 | 10 | 301001 | 4 | 1140 | 母排A过电流 2 | BOOL |  |  |  | X
报警 | 1000 | 10 | 301001 | 4 | 1140 | 主网(市电)过电流 2 | BOOL |  |  |  |  | X
报警 | 1000 | 11 | 301001 | 4 | 1150 | 机组过电压 1 | BOOL | [5 empty] | X
报警 | 1000 | 11 | 301001 | 4 | 1150 | 母排A过电压 1 | BOOL |  |  |  | X
报警 | 1000 | 11 | 301001 | 4 | 1150 | 主网(市电)过电流 1 | BOOL |  |  |  |  | X
报警 | 1000 | 12 | 301001 | 4 | 1160 | 机组过电压 2 | BOOL | [5 empty] | X
报警 | 1000 | 12 | 301001 | 4 | 1160 | 母排A过电压 2 | BOOL |  |  |  | X
报警 | 1000 | 12 | 301001 | 4 | 1160 | 主网(市电)过电流 2 | BOOL |  |  |  |  | X
报警 | 1000 | 13 | 301001 | 4 | 1170 | 机组低电压 1 | BOOL | [5 empty] | X
报警 | 1000 | 13 | 301001 | 4 | 1170 | 母排A低电压 1 | BOOL |  |  |  | X
报警 | 1000 | 13 | 301001 | 4 | 1170 | 主网(市电)低电压 1 | BOOL |  |  |  |  | X
报警 | 1000 | 14 | 301001 | 4 | 1180 | 机组低电压 2 | BOOL | [5 empty] | X
报警 | 1000 | 14 | 301001 | 4 | 1180 | 母排A低电压 2 | BOOL |  |  |  | X
报警 | 1000 | 14 | 301001 | 4 | 1180 | 主网(市电)低电压 2 | BOOL |  |  |  |  | X
报警 | 1000 | 15 | 301001 | 4 | 1190 | 机组低电压 3 | BOOL | [5 empty] | X
报警 | 1000 | 15 | 301001 | 4 | 1190 | 主网(市电)低电压 3 | BOOL |  |  |  |  | X
报警 | 1000 | 15 | 301001 | 4 | 1190 | 母排A低电压 3 | BOOL |  |  |  | X
报警 | 1001 | 0 | 301002 | 4 | 1210 | 机组过频 1 | BOOL | [5 empty] | X
报警 | 1001 | 0 | 301002 | 4 | 1210 | 母排A过频 1 | BOOL |  |  |  | X
报警 | 1001 | 0 | 301002 | 4 | 1210 | 主网(市电)过频 1 | BOOL |  |  |  |  | X
报警 | 1001 | 1 | 301002 | 4 | 1220 | 母排A过频 2 | BOOL |  |  |  | X
报警 | 1001 | 1 | 301002 | 4 | 1220 | 机组过频 2 | BOOL | [5 empty] | X
报警 | 1001 | 1 | 301002 | 4 | 1220 | 主网(市电)过频 2 | BOOL |  |  |  |  | X
报警 | 1001 | 2 | 301002 | 4 | 1230 | 机组过频 3 | BOOL | [5 empty] | X
报警 | 1001 | 2 | 301002 | 4 | 1230 | 母排A过频 3 | BOOL |  |  |  | X
报警 | 1001 | 2 | 301002 | 4 | 1230 | 主网(市电)过频 3 | BOOL |  |  |  |  | X
报警 | 1001 | 3 | 301002 | 4 | 1240 | 母排A欠频 1 | BOOL |  |  |  | X
报警 | 1001 | 3 | 301002 | 4 | 1240 | 机组欠频 1 | BOOL | [5 empty] | X
报警 | 1001 | 3 | 301002 | 4 | 1240 | 主网(市电)欠频 1 | BOOL |  |  |  |  | X
报警 | 1001 | 4 | 301002 | 4 | 1250 | 机组欠频 2 | BOOL | [5 empty] | X
报警 | 1001 | 4 | 301002 | 4 | 1250 | 母排A欠频 2 | BOOL |  |  |  | X
报警 | 1001 | 4 | 301002 | 4 | 1250 | 主网(市电)欠频 2 | BOOL |  |  |  |  | X
报警 | 1001 | 5 | 301002 | 4 | 1260 | 机组欠频 3 | BOOL | [5 empty] | X
报警 | 1001 | 5 | 301002 | 4 | 1260 | 主网(市电)欠频 3 | BOOL |  |  |  |  | X
报警 | 1001 | 5 | 301002 | 4 | 1260 | 母排A欠频 3 | BOOL |  |  |  | X
报警 | 1001 | 6 | 301002 | 4 | 1270 | 母排过电压 1 | BOOL |  |  |  | X | X | X
报警 | 1001 | 7 | 301002 | 4 | 1280 | 母排过电压 2 | BOOL |  |  |  | X | X | X
报警 | 1001 | 8 | 301002 | 4 | 1290 | 母排过电压 3 | BOOL |  |  |  | X | X | X
报警 | 1001 | 9 | 301002 | 4 | 1300 | 母排低电压 1 | BOOL |  |  |  | X | X | X
报警 | 1001 | 10 | 301002 | 4 | 1310 | 母排低电压 2 | BOOL |  |  |  | X | X | X
报警 | 1001 | 11 | 301002 | 4 | 1320 | 母排低电压 3 | BOOL |  |  |  | X | X | X
报警 | 1001 | 12 | 301002 | 4 | 1330 | 母排低电压 4 | BOOL |  |  |  | X | X | X
报警 | 1001 | 13 | 301002 | 4 | 1350 | 母排过频 1 | BOOL |  |  |  | X | X | X
报警 | 1001 | 14 | 301002 | 4 | 1360 | 母排过频 2 | BOOL |  |  |  | X | X | X
报警 | 1001 | 15 | 301002 | 4 | 1370 | 母排过频 3 | BOOL |  |  |  | X | X | X
报警 | 1002 | 0 | 301003 | 4 | 1380 | 母排欠频 1 | BOOL |  |  |  | X | X | X
报警 | 1002 | 1 | 301003 | 4 | 1390 | 母排欠频 2 | BOOL |  |  |  | X | X | X
报警 | 1002 | 2 | 301003 | 4 | 1400 | 母排欠频 3 | BOOL |  |  |  | X | X | X
报警 | 1002 | 3 | 301003 | 4 | 1410 | 母排欠频 4 | BOOL |  |  |  | X | X | X
报警 | 1002 | 4 | 301003 | 4 | 1420 | 频率突变 (ROCOF) | BOOL |  |  |  | X | X | X
报警 | 1002 | 5 | 301003 | 4 | 1430 | 相位突变 | BOOL |  |  |  | X | X | X
报警 | 1002 | 6 | 301003 | 4 | 1440 | 母排正序电压低 | BOOL |  |  |  | X | X | X
报警 | 1002 | 7 | 301003 | 4 | 1450 | 母排A过载 1 | BOOL |  |  |  | X
报警 | 1002 | 7 | 301003 | 4 | 1450 | 机组过载 1 | BOOL | [5 empty] | X
报警 | 1002 | 7 | 301003 | 4 | 1450 | 主网(市电)过载 1 | BOOL |  |  |  |  | X
报警 | 1002 | 8 | 301003 | 4 | 1460 | 机组过载 2 | BOOL | [5 empty] | X
报警 | 1002 | 8 | 301003 | 4 | 1460 | 母排A过载 2 | BOOL |  |  |  | X
报警 | 1002 | 8 | 301003 | 4 | 1460 | 主网(市电)过载 2 | BOOL |  |  |  |  | X
报警 | 1002 | 9 | 301003 | 4 | 1470 | 机组过载 3 | BOOL | [5 empty] | X
报警 | 1002 | 9 | 301003 | 4 | 1470 | 母排A过载 3 | BOOL |  |  |  | X
报警 | 1002 | 9 | 301003 | 4 | 1470 | 主网(市电)过载 3 | BOOL |  |  |  |  | X
报警 | 1002 | 10 | 301003 | 4 | 1480 | 机组过载 4 | BOOL | [5 empty] | X
报警 | 1002 | 10 | 301003 | 4 | 1480 | 母排A过载 4 | BOOL |  |  |  | X
报警 | 1002 | 10 | 301003 | 4 | 1480 | 主网(市电)过载 4 | BOOL |  |  |  |  | X
报警 | 1002 | 11 | 301003 | 4 | 1490 | 机组过载5 | BOOL | [5 empty] | X
报警 | 1002 | 11 | 301003 | 4 | 1490 | 母排A过载 5 | BOOL |  |  |  | X
报警 | 1002 | 11 | 301003 | 4 | 1490 | 主网(市电)过载 5 | BOOL |  |  |  |  | X
报警 | 1002 | 12 | 301003 | 4 | 1500 | 机组不平衡电流1 | BOOL |  |  |  |  | X | X
报警 | 1002 | 13 | 301003 | 4 | 1510 | 电压不平衡 | BOOL |  |  |  |  | X | X
报警 | 1002 | 14 | 301003 | 4 | 1520 | 机组欠励 (逆无功或环流大） | BOOL | [5 empty] | X
报警 | 1002 | 14 | 301003 | 4 | 1520 | 母排A欠励 (逆无功或环流大） | BOOL |  |  |  | X
报警 | 1002 | 14 | 301003 | 4 | 1520 | 主网(市电)欠励 (逆无功或环流大） | BOOL |  |  |  |  | X
报警 | 1002 | 15 | 301003 | 4 | 1530 | 机组过励 | BOOL | [5 empty] | X
报警 | 1002 | 15 | 301003 | 4 | 1530 | 母排A过励 | BOOL |  |  |  | X
报警 | 1002 | 15 | 301003 | 4 | 1530 | 主网(市电)过励 | BOOL |  |  |  |  | X
报警 | 1003 | 0 | 301004 | 4 | 1540 | 机组负序电流报警(I) | BOOL | [5 empty] | X
报警 | 1003 | 0 | 301004 | 4 | 1540 | 主网(市电)负序I报警(I) | BOOL |  |  |  |  | X
报警 | 1003 | 1 | 301004 | 4 | 1550 | 发电机负序U报警(U) | BOOL | [5 empty] | X
报警 | 1003 | 1 | 301004 | 4 | 1550 | 母排A负序U报警(U) | BOOL |  |  |  | X
报警 | 1003 | 1 | 301004 | 4 | 1550 | 主网(市电)负序I报警(U) | BOOL |  |  |  |  | X
报警 | 1003 | 2 | 301004 | 4 | 1570 | 机组零序电流报警(I) | BOOL | [5 empty] | X
报警 | 1003 | 2 | 301004 | 4 | 1570 | 母排A零序电流报警(I) | BOOL |  |  |  | X
报警 | 1003 | 2 | 301004 | 4 | 1570 | 主网(市电)零序电流报警(I) | BOOL |  |  |  |  | X
报警 | 1003 | 3 | 301004 | 4 | 1580 | 机组零序电压报警(U) | BOOL | [5 empty] | X
报警 | 1003 | 3 | 301004 | 4 | 1580 | 母排A零序电流报警(U) | BOOL |  |  |  | X
报警 | 1003 | 3 | 301004 | 4 | 1580 | 主网(市电)零序电流报警(U) | BOOL |  |  |  |  | X
报警 | 1003 | 4 | 301004 | 4 | 1600 | 方向过电流1报警 | BOOL |  |  |  | X | X | X
报警 | 1003 | 5 | 301004 | 4 | 1610 | 方向过电流2报警 | BOOL |  |  |  | X | X | X
报警 | 1003 | 6 | 301004 | 4 | 1620 | 母排电压不平衡报警 | BOOL |  |  |  | X | X | X
报警 | 1003 | 7 | 301004 | 4 | 1800 | 非重要负载1过电流 | BOOL |  |  |  |  | X | X
报警 | 1003 | 8 | 301004 | 4 | 1810 | 非重要负载2过电流 | BOOL |  |  |  |  | X | X
报警 | 1003 | 9 | 301004 | 4 | 1820 | 非重要负载3过电流 | BOOL |  |  |  |  | X | X
报警 | 1003 | 10 | 301004 | 4 | 1830 | 非重要负载1 母排欠频 | BOOL |  |  |  |  | X | X
报警 | 1003 | 11 | 301004 | 4 | 1840 | 非重要负载2 母排欠频 | BOOL |  |  |  |  | X | X
报警 | 1003 | 12 | 301004 | 4 | 1850 | 非重要负载3 母排欠频 | BOOL |  |  |  |  | X | X
报警 | 1003 | 13 | 301004 | 4 | 1860 | 非重要负载1 过载 | BOOL |  |  |  |  | X | X
报警 | 1003 | 14 | 301004 | 4 | 1870 | 非重要负载2 过载 | BOOL |  |  |  |  | X | X
报警 | 1003 | 15 | 301004 | 4 | 1880 | 非重要负载3 过载 | BOOL |  |  |  |  | X | X
报警 | 1004 | 0 | 301005 | 4 | 1890 | 非重要负载 1 | BOOL |  |  |  |  | X | X
报警 | 1004 | 1 | 301005 | 4 | 1900 | 非重要负载 2 | BOOL |  |  |  |  | X | X
报警 | 1004 | 2 | 301005 | 4 | 1910 | 非重要负载 3 | BOOL |  |  |  |  | X | X
报警 | 1004 | 6 | 301005 | 4 | 1960 | 欠电压及低无功保护1（U and Q< 1） | BOOL |  |  |  |  | X | X
报警 | 1004 | 7 | 301005 | 4 | 1970 | 欠电压及低无功保护1（U and Q< 2） | BOOL |  |  |  |  | X | X
报警 | 1004 | 8 | 301005 | 4 | 1981 | 机组外部跳闸 | BOOL | [5 empty] | X
报警 | 1004 | 8 | 301005 | 4 | 1981 | BTB 外部跳闸 | BOOL |  |  |  | X
报警 | 1004 | 8 | 301005 | 4 | 1981 | TB 外部跳闸 | BOOL |  |  |  |  | X
报警 | 1004 | 9 | 301005 | 4 | 1983 | MB 外部跳闸 | BOOL |  |  |  |  | X | X
报警 | 1004 | 10 | 301005 | 4 | 1650 | UT <1 监测激活 | BOOL | [5 empty] | X
报警 | 1004 | 11 | 301005 | 4 | 1660 | UT <1 | BOOL | [5 empty] | X
报警 | 1004 | 12 | 301005 | 4 | 1690 | UT <2 监测激活 | BOOL | [5 empty] | X
报警 | 1004 | 13 | 301005 | 4 | 1700 | UT <2 | BOOL | [5 empty] | X
报警 | 1004 | 14 | 301005 | 4 | 1760 | 基于有功的欠无功 | BOOL | [5 empty] | X
报警 | 1004 | 15 | 301005 | 4 | 1790 | 基于有功的过无功 | BOOL | [5 empty] | X
报警 | 1005 | 0 | 301006 | 4 | 2120 | 同步窗口报警 | BOOL |  |  |  | X | X | X
报警 | 1005 | 1 | 301006 | 4 | 2130 | 同步故障 GB | BOOL | [5 empty] | X
报警 | 1005 | 1 | 301006 | 4 | 2130 | 同步故障 BTB | BOOL |  |  |  | X
报警 | 1005 | 1 | 301006 | 4 | 2130 | 同步故障 TB | BOOL |  |  |  |  | X
报警 | 1005 | 2 | 301006 | 4 | 2140 | 同步故障 MB | BOOL |  |  |  |  | X | X
报警 | 1005 | 3 | 301006 | 4 | 2150 | 相序出错 A | BOOL |  |  |  | X | X | X
报警 | 1005 | 4 | 301006 | 4 | 2160 | GB 分闸失败 | BOOL | [5 empty] | X
报警 | 1005 | 4 | 301006 | 4 | 2160 | BTB分闸失败 | BOOL |  |  |  | X
报警 | 1005 | 4 | 301006 | 4 | 2160 | TB分闸失败 | BOOL |  |  |  |  | X
报警 | 1005 | 5 | 301006 | 4 | 2170 | BTB合闸失败 | BOOL |  |  |  | X
报警 | 1005 | 5 | 301006 | 4 | 2170 | GB 合闸失败 | BOOL | [5 empty] | X
报警 | 1005 | 5 | 301006 | 4 | 2170 | TB 合闸失败 | BOOL |  |  |  |  | X
报警 | 1005 | 6 | 301006 | 4 | 2180 | BTB 位置反馈故障 | BOOL |  |  |  | X
报警 | 1005 | 6 | 301006 | 4 | 2180 | GB 位置反馈故障 | BOOL | [5 empty] | X
报警 | 1005 | 6 | 301006 | 4 | 2180 | TB 位置反馈故障 | BOOL |  |  |  |  | X
报警 | 1005 | 7 | 301006 | 4 | 2200 | MB 分闸失败 | BOOL |  |  |  |  | X | X
报警 | 1005 | 8 | 301006 | 4 | 2210 | MB 合闸失败 | BOOL |  |  |  |  | X | X
报警 | 1005 | 9 | 301006 | 4 | 2220 | MB 位置反馈故障 | BOOL |  |  |  |  | X | X
报警 | 1005 | 10 | 301006 | 4 | 2270 | CBE失败 | BOOL | [5 empty] | X
报警 | 1005 | 11 | 301006 | 4 | 2155 | 相序出错 B | BOOL |  |  |  | X | X | X
报警 | 1006 | 0 | 301007 | 4 | 2560 | 调速失败 | BOOL | [5 empty] | X
报警 | 1006 | 1 | 301007 | 4 | 2630 | 解列失败 | BOOL | [5 empty] | X
报警 | 1006 | 2 | 301007 | 4 | 2680 | 调压失败 | BOOL | [5 empty] | X
报警 | 1007 | 0 | 301008 | 4 | 3000 | 开关量报警输入点 77 | BOOL |  |  |  | X | X | X
报警 | 1007 | 1 | 301008 | 4 | 3010 | 开关量报警输入点 78 | BOOL |  |  |  | X | X | X
报警 | 1007 | 2 | 301008 | 4 | 3020 | 开关量报警输入点 79 | BOOL |  |  |  | X | X | X
报警 | 1007 | 3 | 301008 | 4 | 3030 | 开关量报警输入点 80 | BOOL |  |  |  | X | X | X
报警 | 1007 | 4 | 301008 | 4 | 3040 | 开关量报警输入点 81 | BOOL |  |  |  | X | X | X
报警 | 1007 | 5 | 301008 | 4 | 3050 | 开关量报警输入点 82 | BOOL |  |  |  | X | X | X
报警 | 1007 | 6 | 301008 | 4 | 3060 | 开关量报警输入点 83 | BOOL |  |  |  | X | X | X
报警 | 1007 | 7 | 301008 | 4 | 3070 | 开关量报警输入点 84 | BOOL |  |  |  | X | X | X
报警 | 1007 | 8 | 301008 | 4 | 3080 | 开关量报警输入点 85 | BOOL |  |  |  | X | X | X
报警 | 1007 | 9 | 301008 | 4 | 3090 | 开关量报警输入点 86 | BOOL |  |  |  | X | X | X
报警 | 1007 | 10 | 301008 | 4 | 3100 | 开关量报警输入点 87 | BOOL |  |  |  | X | X | X
报警 | 1007 | 11 | 301008 | 4 | 3110 | 开关量报警输入点 88 | BOOL |  |  |  | X | X | X
报警 | 1007 | 12 | 301008 | 4 | 3120 | 开关量报警输入点 89 | BOOL |  |  |  | X | X | X
报警 | 1008 | 0 | 301009 | 4 | 3130 | 开关量报警输入点 90 | BOOL |  |  |  | X | X | X
报警 | 1010 | 0 | 301011 | 4 | 3400 | 多功能输入报警 46 | BOOL |  |  |  | X | X | X
报警 | 1010 | 1 | 301011 | 4 | 3410 | 多功能输入报警 47 | BOOL |  |  |  | X | X | X
报警 | 1010 | 2 | 301011 | 4 | 3420 | 多功能输入报警 48 | BOOL |  |  |  | X | X | X
报警 | 1010 | 3 | 301011 | 4 | 3401 | 断线报警46 | BOOL |  |  |  | X | X | X
报警 | 1010 | 4 | 301011 | 4 | 3411 | 断线报警47 | BOOL |  |  |  | X | X | X
报警 | 1010 | 5 | 301011 | 4 | 3421 | 断线报警48 | BOOL |  |  |  | X | X | X
报警 | 1010 | 12 | 301011 | 4 | 3490 | 开关量报警输入点 25（急停） | BOOL |  |  |  | X | X | X
报警 | 1011 | 7 | 301012 | 4 | 3570 | M-Logic逻辑编程报警 1 | BOOL |  |  |  | X | X | X
报警 | 1011 | 8 | 301012 | 4 | 3580 | M-Logic逻辑编程报警 2 | BOOL |  |  |  | X | X | X
报警 | 1011 | 9 | 301012 | 4 | 3590 | M-Logic逻辑编程报警 3 | BOOL |  |  |  | X | X | X
报警 | 1011 | 10 | 301012 | 4 | 3600 | M-Logic逻辑编程报警 4 | BOOL |  |  |  | X | X | X
报警 | 1011 | 11 | 301012 | 4 | 3610 | M-Logic逻辑编程报警 5 | BOOL |  |  |  | X | X | X
报警 | 1013 | 0 | 301014 | 4 | 4120, 4140, 4160, 4180, 4200, 4220 | 多功能输入端 46.1 | BOOL |  |  |  | X | X | X
报警 | 1013 | 1 | 301014 | 4 | 4130, 4150, 4170, 4190, 4210, 4230 | 多功能输入端 46.2 | BOOL |  |  |  | X | X | X
报警 | 1013 | 2 | 301014 | 4 | 4240 | 断线报警46 | BOOL |  |  |  | X | X | X
报警 | 1013 | 3 | 301014 | 4 | 4250, 4270, 4290, 4310, 4330, 4350 | 多功能输入端 47.1 | BOOL |  |  |  | X | X | X
报警 | 1013 | 4 | 301014 | 4 | 4260, 4280, 4300, 4320, 4340, 4360 | 多功能输入端 47.2 | BOOL |  |  |  | X | X | X
报警 | 1013 | 5 | 301014 | 4 | 4370 | 断线报警47 | BOOL |  |  |  | X | X | X
报警 | 1013 | 6 | 301014 | 4 | 4380, 4400, 4420, 4440, 4460, 4480 | 多功能输入端 48.1 | BOOL |  |  |  | X | X | X
报警 | 1013 | 7 | 301014 | 4 | 4390, 4410, 4430, 4450, 4470, 4490 | 多功能输入端 48.2 | BOOL |  |  |  | X | X | X
报警 | 1013 | 8 | 301014 | 4 | 4500 | 断线报警48 | BOOL |  |  |  | X | X | X
报警 | 1013 | 9 | 301014 | 4 | 4510 | 超速1 | BOOL | [5 empty] | X
报警 | 1013 | 10 | 301014 | 4 | 4520 | 超速 2 | BOOL | [5 empty] | X
报警 | 1013 | 11 | 301014 | 4 | 4530 | 盘车失败 | BOOL | [5 empty] | X
报警 | 1013 | 12 | 301014 | 4 | 4540 | 运行反馈出错 | BOOL | [5 empty] | X
报警 | 1013 | 13 | 301014 | 4 | 4550 | 测试传感器断线 | BOOL | [5 empty] | X
报警 | 1013 | 14 | 301014 | 4 | 4560 | 频率/电压故障 | BOOL | [5 empty] | X
报警 | 1013 | 15 | 301014 | 4 | 4570 | 启动失败 | BOOL | [5 empty] | X
报警 | 1014 | 0 | 301015 | 4 | 4580 | 停机失败 | BOOL | [5 empty] | X
报警 | 1014 | 1 | 301015 | 4 | 4960 | 电源电压低1 | BOOL |  |  |  | X | X | X
报警 | 1014 | 2 | 301015 | 4 | 4970 | 电源电压高1 | BOOL |  |  |  | X | X | X
报警 | 1014 | 5 | 301015 | 4 | 4590 | 欠速 1 | BOOL | [5 empty] | X
报警 | 1015 | 0 | 301016 | 4 | 6110 | 保养周期 1 | BOOL | [5 empty] | X
报警 | 1015 | 1 | 301016 | 4 | 6120 | 保养周期 2 | BOOL | [5 empty] | X
报警 | 1015 | 2 | 301016 | 4 | 6270 | 停止线圈(Stop coi) 断线 | BOOL | [5 empty] | X
报警 | 1015 | 4 | 301016 | 4 | 6330 | 机组预热报警1 | BOOL | [5 empty] | X
报警 | 1015 | 5 | 301016 | 4 | 6410 | 电池测试激活 | BOOL | [5 empty] | X
报警 | 1015 | 6 | 301016 | 4 | 6440 | 电池电压不对称报警1 | BOOL | [5 empty] | X
报警 | 1015 | 7 | 301016 | 4 | 6450 | 电池电压不对称报警2 | BOOL | [5 empty] | X
报警 | 1015 | 8 | 301016 | 4 | 6470 | 最大通风报警1 | BOOL | [5 empty] | X
报警 | 1015 | 9 | 301016 | 4 | 6480 | 最大通风报警2 | BOOL | [5 empty] | X
报警 | 1015 | 10 | 301016 | 4 | 6500 | 配电盘出错阻止起动（Blk. swbd. Error） | BOOL | [5 empty] | X
报警 | 1015 | 11 | 301016 | 4 | 6510 | 配电盘出错分闸冷却停机（Stp. swbd. error） | BOOL | [5 empty] | X
报警 | 1015 | 12 | 301016 | 4 | 6540 | 模块不在自动 | BOOL |  |  |  | X | X | X
报警 | 1015 | 13 | 301016 | 4 | 6550 | 燃油泵逻辑错报警 | BOOL | [5 empty] | X
报警 | 1016 | 0 | 301017 | 4 | 5000 | 继电器 16 | BOOL |  |  |  | X | X | X
报警 | 1016 | 1 | 301017 | 4 | 5010 | 继电器 18 | BOOL |  |  |  | X | X | X
报警 | 1016 | 2 | 301017 | 4 | 5020 | 继电器 20 | BOOL |  |  |  | X | X | X
报警 | 1016 | 3 | 301017 | 4 | 5030 | 继电器 23 | BOOL |  |  |  | X | X | X
报警 | 1016 | 4 | 301017 | 4 | 5040 | 继电器 26 | BOOL |  |  |  | X | X | X
报警 | 1016 | 5 | 301017 | 4 | 5050 | 继电器 27 | BOOL |  |  |  | X | X | X
报警 | 1016 | 6 | 301017 | 4 | 5060 | 继电器 28 | BOOL |  |  |  | X | X | X
报警 | 1016 | 7 | 301017 | 4 | 5070 | 继电器 30 | BOOL |  |  |  | X | X | X
报警 | 1016 | 8 | 301017 | 4 | 5080 | 继电器 32 | BOOL |  |  |  | X | X | X
报警 | 1016 | 9 | 301017 | 4 | 8090 | 继电器 34 | BOOL |  |  |  | X | X | X
报警 | 1016 | 10 | 301017 | 4 | 5100 | 继电器 36 | BOOL |  |  |  | X | X | X
报警 | 1016 | 11 | 301017 | 4 | 5110 | 继电器 39 | BOOL |  |  |  | X | X | X
报警 | 1016 | 12 | 301017 | 4 | 5120 | 继电器 41 | BOOL |  |  |  | X | X | X
报警 | 1016 | 13 | 301017 | 4 | 5130 | 继电器 43 | BOOL |  |  |  | X | X | X
报警 | 1017 | 12 | 301018 | 4 |  | 运行继电器 | BOOL | [5 empty] | X
报警 | 1017 | 13 | 301018 | 4 |  | 预供或预润滑（Start prepare） | BOOL | [5 empty] | X
报警 | 1017 | 14 | 301018 | 4 |  | 启动继电器 | BOOL | [5 empty] | X
报警 | 1017 | 15 | 301018 | 4 |  | 停止继电器 | BOOL | [5 empty] | X
报警 | 1018 | 0 | 301019 | 4 |  | 市电(主网)故障 | BOOL |  |  |  |  | X | X
报警 | 1018 | 1 | 301019 | 4 |  | 市电位置反馈ON | BOOL |  |  |  |  | X | X
报警 | 1018 | 2 | 301019 | 4 |  | 机组减载 | BOOL | [5 empty] | X
报警 | 1018 | 3 | 301019 | 4 |  | 开始调速调压 | BOOL | [5 empty] | X
报警 | 1018 | 4 | 301019 | 4 |  | GB位置反馈ON | BOOL | [5 empty] | X
报警 | 1018 | 4 | 301019 | 4 |  | TB位置反馈ON | BOOL |  |  |  |  | X
报警 | 1018 | 4 | 301019 | 4 |  | BTB位置反馈ON | BOOL |  |  |  | X
报警 | 1018 | 5 | 301019 | 4 |  | GB 正在同步 | BOOL | [5 empty] | X
报警 | 1018 | 5 | 301019 | 4 |  | BTB正在同步 | BOOL |  |  |  | X
报警 | 1018 | 5 | 301019 | 4 |  | TB正在同步 | BOOL |  |  |  |  | X
报警 | 1018 | 6 | 301019 | 4 |  | 机组运行 | BOOL | [5 empty] | X
报警 | 1018 | 7 | 301019 | 4 | 6173 | 运行侦测计时到 | BOOL | [5 empty] | X
报警 | 1018 | 8 | 301019 | 4 | 6220 | 机组频率/电压 OK计时到 | BOOL | [5 empty] | X
报警 | 1018 | 8 | 301019 | 4 | 6220 | 母排频率/电压OK 计时到 | BOOL |  |  |  | X | X
报警 | 1018 | 9 | 301019 | 4 | 6410 | 电池测试进行中 | BOOL | [5 empty] | X
报警 | 1018 | 11 | 301019 | 4 |  | 机组开关位置OFF | BOOL | [5 empty] | X
报警 | 1018 | 11 | 301019 | 4 |  | BTB开关位置OFF | BOOL |  |  |  | X
报警 | 1018 | 11 | 301019 | 4 |  | TB开关位置OFF | BOOL |  |  |  |  | X
报警 | 1018 | 12 | 301019 | 4 |  | MB开关位置OFF | BOOL |  |  |  |  | X | X
报警 | 1018 | 13 | 301019 | 4 |  | 母排频率/电压OK | BOOL |  |  |  | X | X | X
报警 | 1018 | 14 | 301019 | 4 |  | 单个DG, MB正在同步 | BOOL | [5 empty] | X
报警 | 1018 | 15 | 301019 | 4 |  | AVR烘干模式 | BOOL | [5 empty] | X
报警 | 1019 | 0 | 301020 | 4 |  | 检修模式（Block mode） | BOOL |  |  |  | X | X | X
报警 | 1019 | 1 | 301020 | 4 |  | 手动模式（Man） | BOOL | [5 empty] | X
报警 | 1019 | 2 | 301020 | 4 |  | 半自动模式（Semi auto mode） | BOOL |  |  |  | X | X | X
报警 | 1019 | 3 | 301020 | 4 |  | 自动模式（Auto） | BOOL |  |  |  | X | X | X
报警 | 1019 | 4 | 301020 | 4 |  | 测试模式（Test） | BOOL |  |  |  |  | X | X
报警 | 1019 | 5 | 301020 | 4 |  | 单机（Island） | BOOL |  |  |  |  | X | X
报警 | 1019 | 6 | 301020 | 4 |  | 市电自动失效（AMF） | BOOL |  |  |  |  | X | X
报警 | 1019 | 7 | 301020 | 4 |  | 调峰（Peak shaving） | BOOL |  |  |  |  | X | X
报警 | 1019 | 8 | 301020 | 4 |  | 固定功率（Fixed ） | BOOL |  |  |  |  | X | X
报警 | 1019 | 9 | 301020 | 4 |  | 主网(市电) 功率 输出（MPE) | BOOL |  |  |  |  | X | X
报警 | 1019 | 10 | 301020 | 4 |  | 负载轮换（Load takeover） | BOOL |  |  |  |  | X | X
报警 | 1019 | 11 | 301020 | 4 |  | 功率管理（Power management） | BOOL | [5 empty] | X
报警 | 1019 | 15 | 301020 | 4 |  | AMF 激活 | BOOL |  |  |  |  | X | X
报警 | 1020 | 0 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 1 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 2 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 3 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 4 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 5 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 6 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 7 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 8 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 9 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 10 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 11 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 12 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1020 | 13 | 301021 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1021 | 0 | 301022 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1021 | 1 | 301022 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1021 | 12 | 301022 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1021 | 13 | 301022 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1021 | 14 | 301022 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1021 | 15 | 301022 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 0 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 1 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 2 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 3 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 4 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 5 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 6 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 7 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 8 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 9 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 10 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 11 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 12 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 13 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 14 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1022 | 15 | 301023 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 0 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 1 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 2 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 3 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 4 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 5 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 6 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 7 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 8 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 9 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 10 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 11 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 12 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 13 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 14 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1023 | 15 | 301024 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 0 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 1 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 2 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 3 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 4 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 5 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 6 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 7 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 8 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 9 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 10 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 11 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 12 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 13 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 14 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1024 | 15 | 301025 | 4 |  | 见 设计参考手册 | BOOL | [5 empty] | X
报警 | 1026 | 0 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 1 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 2 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 3 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 4 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 5 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 6 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 7 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 8 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 9 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 10 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 11 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 12 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 13 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 14 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1026 | 15 | 301027 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 0 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 1 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 2 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 3 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 4 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 5 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 6 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 7 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 8 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 9 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 10 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 11 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 12 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 13 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 14 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1027 | 15 | 301028 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1028 | 0 | 301029 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1028 | 1 | 301029 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1028 | 2 | 301029 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1028 | 3 | 301029 | 4 |  | 请参见 H5/H7 手册 | BOOL | [5 empty] | X
报警 | 1031 | 1 | 301032 | 4 |  | CAN 1 离线 ID 1 | BOOL |  |  |  | X | X | X
报警 | 1031 | 2 | 301032 | 4 |  | CAN 1 离线 ID 2 | BOOL |  |  |  | X | X | X
报警 | 1031 | 3 | 301032 | 4 |  | CAN 1 离线 ID 3 | BOOL |  |  |  | X | X | X
报警 | 1031 | 4 | 301032 | 4 |  | CAN 1 离线 ID 4 | BOOL |  |  |  | X | X | X
报警 | 1031 | 5 | 301032 | 4 |  | CAN 1 离线 ID 5 | BOOL |  |  |  | X | X | X
报警 | 1031 | 6 | 301032 | 4 |  | CAN 1 离线 ID 6 | BOOL |  |  |  | X | X | X
报警 | 1031 | 7 | 301032 | 4 |  | CAN 1 离线 ID 7 | BOOL |  |  |  | X | X | X
报警 | 1031 | 8 | 301032 | 4 |  | CAN 1 离线 ID 8 | BOOL |  |  |  | X | X | X
报警 | 1031 | 9 | 301032 | 4 |  | CAN 1 离线 ID 9 | BOOL |  |  |  | X | X | X
报警 | 1031 | 10 | 301032 | 4 |  | CAN 1 离线 ID 10 | BOOL |  |  |  | X | X | X
报警 | 1031 | 11 | 301032 | 4 |  | CAN 1 离线 ID 11 | BOOL |  |  |  | X | X | X
报警 | 1031 | 12 | 301032 | 4 |  | CAN 1 离线 ID 12 | BOOL |  |  |  | X | X | X
报警 | 1031 | 13 | 301032 | 4 |  | CAN 1 离线 ID 13 | BOOL |  |  |  | X | X | X
报警 | 1031 | 14 | 301032 | 4 |  | CAN 1 离线 ID 14 | BOOL |  |  |  | X | X | X
报警 | 1031 | 15 | 301032 | 4 |  | CAN 1 离线 ID 15 | BOOL |  |  |  | X | X | X
报警 | 1032 | 0 | 301033 | 4 |  | CAN 1 离线 ID 16 | BOOL |  |  |  | X | X | X
报警 | 1032 | 2 | 301033 | 4 |  | CAN 2离线ID 1 | BOOL |  |  |  | X | X | X
报警 | 1032 | 3 | 301033 | 4 |  | CAN 2离线D 2 | BOOL |  |  |  | X | X | X
报警 | 1032 | 4 | 301033 | 4 |  | CAN 2离线ID 3 | BOOL |  |  |  | X | X | X
报警 | 1032 | 5 | 301033 | 4 |  | CAN 2离线ID 4 | BOOL |  |  |  | X | X | X
报警 | 1032 | 6 | 301033 | 4 |  | CAN 2离线ID 5 | BOOL |  |  |  | X | X | X
报警 | 1032 | 7 | 301033 | 4 |  | CAN 2离线ID 6 | BOOL |  |  |  | X | X | X
报警 | 1032 | 8 | 301033 | 4 |  | CAN 2离线ID 7 | BOOL |  |  |  | X | X | X
报警 | 1032 | 9 | 301033 | 4 |  | CAN 2离线ID 8 | BOOL |  |  |  | X | X | X
报警 | 1032 | 10 | 301033 | 4 |  | CAN 2离线ID 9 | BOOL |  |  |  | X | X | X
报警 | 1032 | 11 | 301033 | 4 |  | CAN 2离线ID 10 | BOOL |  |  |  | X | X | X
报警 | 1032 | 12 | 301033 | 4 |  | CAN 2离线ID 11 | BOOL |  |  |  | X | X | X
报警 | 1032 | 13 | 301033 | 4 |  | CAN 2离线ID 12 | BOOL |  |  |  | X | X | X
报警 | 1032 | 14 | 301033 | 4 |  | CAN 2离线ID 13 | BOOL |  |  |  | X | X | X
报警 | 1032 | 15 | 301033 | 4 |  | CAN 2离线ID 14 | BOOL |  |  |  | X | X | X
报警 | 1033 | 0 | 301034 | 4 |  | CAN 2离线ID 16 | BOOL |  |  |  | X | X | X
报警 | 1033 | 1 | 301034 | 4 |  | CAN 2离线ID 15 | BOOL |  |  |  | X | X | X
报警 | 1033 | 2 | 301034 | 4 | 7520 | Modbus/profibus通信出错 | BOOL |  |  |  | X | X | X
报警 | 1034 | 1 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 1 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 1 | BOOL |  |  |  | X | X | X
报警 | 1034 | 2 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 2 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 2 | BOOL |  |  |  | X | X | X
报警 | 1034 | 3 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 3 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 3 | BOOL |  |  |  | X | X | X
报警 | 1034 | 4 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 4 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 4 | BOOL |  |  |  | X | X | X
报警 | 1034 | 5 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 5 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 5 | BOOL |  |  |  | X | X | X
报警 | 1034 | 6 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 6 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 6 | BOOL |  |  |  | X | X | X
报警 | 1034 | 7 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 7 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 7 | BOOL |  |  |  | X | X | X
报警 | 1034 | 8 | 301035 | 4 |  | 外部MODBUS通信出错 on AN ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 8 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 8 | BOOL |  |  |  | X | X | X
报警 | 1034 | 9 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 9 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 9 | BOOL |  |  |  | X | X | X
报警 | 1034 | 10 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 10 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 10 | BOOL |  |  |  | X | X | X
报警 | 1034 | 11 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 11 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 11 | BOOL |  |  |  | X | X | X
报警 | 1034 | 12 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 12 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 12 | BOOL |  |  |  | X | X | X
报警 | 1034 | 13 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 13 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 13 | BOOL |  |  |  | X | X | X
报警 | 1034 | 14 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 14 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 14 | BOOL |  |  |  | X | X | X
报警 | 1034 | 15 | 301035 | 4 |  | 外部MODBUS通信出错 on CAN ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1034 | 15 | 301035 | 4 |  | 外部MODBUS通信出错，CAN ID 15 | BOOL |  |  |  | X | X | X
报警 | 1035 | 0 | 301036 | 4 |  | 外部MODBUS通信出错 on CAN ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1035 | 0 | 301036 | 4 |  | 外部MODBUS通信出错，CAN ID 16 | BOOL |  |  |  | X | X | X
报警 | 1036 | 0 | 301037 | 4 | 12000 | 外部模拟量输入1.1 | BOOL |  |  |  | X | X | X
报警 | 1036 | 1 | 301037 | 4 | 12010 | 外部模拟量输入1.2 | BOOL |  |  |  | X | X | X
报警 | 1036 | 3 | 301037 | 4 | 12030 | 外部模拟量输入2.1 | BOOL |  |  |  | X | X | X
报警 | 1036 | 4 | 301037 | 4 | 12040 | 外部模拟量输入2.2 | BOOL |  |  |  | X | X | X
报警 | 1036 | 6 | 301037 | 4 | 12060 | 外部模拟量输入3.1 | BOOL |  |  |  | X | X | X
报警 | 1036 | 7 | 301037 | 4 | 12070 | 外部模拟量输入3.2 | BOOL |  |  |  | X | X | X
报警 | 1036 | 9 | 301037 | 4 | 12090 | 外部模拟量输入4.1 | BOOL |  |  |  | X | X | X
报警 | 1036 | 10 | 301037 | 4 | 12100 | 外部模拟量输入4.2 | BOOL |  |  |  | X | X | X
报警 | 1036 | 12 | 301037 | 4 | 12120 | 外部模拟量输入5.1 | BOOL |  |  |  | X | X | X
报警 | 1036 | 13 | 301037 | 4 | 12130 | 外部模拟量输入5.2 | BOOL |  |  |  | X | X | X
报警 | 1036 | 15 | 301037 | 4 | 12150 | 外部模拟量输入6.1 | BOOL |  |  |  | X | X | X
报警 | 1037 | 0 | 301038 | 4 | 12160 | 外部模拟量输入6.2 | BOOL |  |  |  | X | X | X
报警 | 1037 | 2 | 301038 | 4 | 12180 | 外部模拟量输入7.1 | BOOL |  |  |  | X | X | X
报警 | 1037 | 3 | 301038 | 4 | 12190 | 外部模拟量输入7.2 | BOOL |  |  |  | X | X | X
报警 | 1037 | 5 | 301038 | 4 | 12210 | 外部模拟量输入8.1 | BOOL |  |  |  | X | X | X
报警 | 1037 | 6 | 301038 | 4 | 12220 | 外部模拟量输入8.2 | BOOL |  |  |  | X | X | X
报警 | 1038 | 0 | 301039 | 4 | 12540 | 扩展 输入点状态位 1 | BOOL |  |  |  | X | X | X
报警 | 1038 | 1 | 301039 | 4 | 12550 | 扩展 输入点状态位 2 | BOOL |  |  |  | X | X | X
报警 | 1038 | 2 | 301039 | 4 | 12560 | 扩展 输入点状态位 3 | BOOL |  |  |  | X | X | X
报警 | 1038 | 3 | 301039 | 4 | 12570 | 扩展 输入点状态位 4 | BOOL |  |  |  | X | X | X
报警 | 1038 | 4 | 301039 | 4 | 12580 | 扩展 输入点状态位 5 | BOOL |  |  |  | X | X | X
报警 | 1038 | 5 | 301039 | 4 | 12590 | 扩展 输入点状态位 6 | BOOL |  |  |  | X | X | X
报警 | 1038 | 6 | 301039 | 4 | 12600 | 扩展 输入点状态位 7 | BOOL |  |  |  | X | X | X
报警 | 1038 | 7 | 301039 | 4 | 12610 | 扩展 输入点状态位 8 | BOOL |  |  |  | X | X | X
报警 | 1038 | 8 | 301039 | 4 | 12620 | 扩展 输入点状态位 9 | BOOL |  |  |  | X | X | X
报警 | 1038 | 9 | 301039 | 4 | 12630 | 扩展 输入点状态位 10 | BOOL |  |  |  | X | X | X
报警 | 1038 | 10 | 301039 | 4 | 12640 | 扩展 输入点状态位 11 | BOOL |  |  |  | X | X | X
报警 | 1038 | 11 | 301039 | 4 | 12650 | 扩展 输入点状态位 12 | BOOL |  |  |  | X | X | X
报警 | 1038 | 12 | 301039 | 4 | 12660 | 扩展 输入点状态位 13 | BOOL |  |  |  | X | X | X
报警 | 1038 | 13 | 301039 | 4 | 12670 | 扩展 输入点状态位 14 | BOOL |  |  |  | X | X | X
报警 | 1038 | 14 | 301039 | 4 | 12680 | 扩展 输入点状态位 15 | BOOL |  |  |  | X | X | X
报警 | 1038 | 15 | 301039 | 4 | 12690 | 扩展 输入点状态位 16 | BOOL |  |  |  | X | X | X
报警 | 1039 | 0 | 301040 | 4 | 12790 | 扩展 开关量输出1 | BOOL |  |  |  | X | X | X
报警 | 1039 | 1 | 301040 | 4 | 12800 | 扩展 开关量输出2 | BOOL |  |  |  | X | X | X
报警 | 1039 | 2 | 301040 | 4 | 12810 | 扩展 开关量输出3 | BOOL |  |  |  | X | X | X
报警 | 1039 | 3 | 301040 | 4 | 12820 | 扩展 开关量输出4 | BOOL |  |  |  | X | X | X
报警 | 1039 | 4 | 301040 | 4 | 12830 | 扩展 开关量输出5 | BOOL |  |  |  | X | X | X
报警 | 1039 | 5 | 301040 | 4 | 12840 | 扩展 开关量输出6 | BOOL |  |  |  | X | X | X
报警 | 1039 | 6 | 301040 | 4 | 12850 | 扩展 开关量输出7 | BOOL |  |  |  | X | X | X
报警 | 1039 | 7 | 301040 | 4 | 12860 | 扩展 开关量输出8 | BOOL |  |  |  | X | X | X
报警 | 1039 | 8 | 301040 | 4 | 12870 | 扩展 开关量输出9 | BOOL |  |  |  | X | X | X
报警 | 1039 | 9 | 301040 | 4 | 12880 | 扩展 开关量输出10 | BOOL |  |  |  | X | X | X
报警 | 1039 | 10 | 301040 | 4 | 12890 | 扩展 开关量输出11 | BOOL |  |  |  | X | X | X
报警 | 1039 | 11 | 301040 | 4 | 12900 | 扩展 开关量输出12 | BOOL |  |  |  | X | X | X
报警 | 1039 | 12 | 301040 | 4 | 12910 | 扩展 开关量输出13 | BOOL |  |  |  | X | X | X
报警 | 1039 | 13 | 301040 | 4 | 12920 | 扩展 开关量输出14 | BOOL |  |  |  | X | X | X
报警 | 1039 | 14 | 301040 | 4 | 12930 | 扩展 开关量输出15 | BOOL |  |  |  | X | X | X
报警 | 1039 | 15 | 301040 | 4 | 12940 | 扩展 开关量输出16 | BOOL |  |  |  | X | X | X
报警 | 1040 | 0 | 301041 | 4 |  | CAN 1 离线 ID 1 | BOOL |  |  |  | X | X | X
报警 | 1040 | 1 | 301041 | 4 |  | CAN 1 离线 ID 2 | BOOL |  |  |  | X | X | X
报警 | 1040 | 2 | 301041 | 4 |  | CAN 1 离线 ID 3 | BOOL |  |  |  | X | X | X
报警 | 1040 | 3 | 301041 | 4 |  | CAN 1 离线 ID 4 | BOOL |  |  |  | X | X | X
报警 | 1040 | 4 | 301041 | 4 |  | CAN 1 离线 ID 5 | BOOL |  |  |  | X | X | X
报警 | 1040 | 5 | 301041 | 4 |  | CAN 1 离线 ID 6 | BOOL |  |  |  | X | X | X
报警 | 1040 | 6 | 301041 | 4 |  | CAN 1 离线 ID 7 | BOOL |  |  |  | X | X | X
报警 | 1040 | 7 | 301041 | 4 |  | CAN 1 离线 ID 8 | BOOL |  |  |  | X | X | X
报警 | 1040 | 8 | 301041 | 4 |  | CAN 1 离线 ID 9 | BOOL |  |  |  | X | X | X
报警 | 1040 | 9 | 301041 | 4 |  | CAN 1 离线 ID 10 | BOOL |  |  |  | X | X | X
报警 | 1040 | 10 | 301041 | 4 |  | CAN 1 离线 ID 11 | BOOL |  |  |  | X | X | X
报警 | 1040 | 11 | 301041 | 4 |  | CAN 1 离线 ID 12 | BOOL |  |  |  | X | X | X
报警 | 1040 | 12 | 301041 | 4 |  | CAN 1 离线 ID 13 | BOOL |  |  |  | X | X | X
报警 | 1040 | 13 | 301041 | 4 |  | CAN 1 离线 ID 14 | BOOL |  |  |  | X | X | X
报警 | 1040 | 14 | 301041 | 4 |  | CAN 1 离线 ID 15 | BOOL |  |  |  | X | X | X
报警 | 1040 | 15 | 301041 | 4 |  | CAN 1 离线 ID 16 | BOOL |  |  |  | X | X | X
报警 | 1041 | 0 | 301042 | 4 |  | CAN 1 离线 ID 17 | BOOL |  |  |  | X | X | X
报警 | 1041 | 1 | 301042 | 4 |  | CAN 1 离线 ID 18 | BOOL |  |  |  | X | X | X
报警 | 1041 | 2 | 301042 | 4 |  | CAN 1 离线 ID 19 | BOOL |  |  |  | X | X | X
报警 | 1041 | 3 | 301042 | 4 |  | CAN 1 离线 ID 20 | BOOL |  |  |  | X | X | X
报警 | 1041 | 4 | 301042 | 4 |  | CAN 1 离线 ID 21 | BOOL |  |  |  | X | X | X
报警 | 1041 | 5 | 301042 | 4 |  | CAN 1 离线 ID 22 | BOOL |  |  |  | X | X | X
报警 | 1041 | 6 | 301042 | 4 |  | CAN 1 离线 ID 23 | BOOL |  |  |  | X | X | X
报警 | 1041 | 7 | 301042 | 4 |  | CAN 1 离线 ID 24 | BOOL |  |  |  | X | X | X
报警 | 1041 | 8 | 301042 | 4 |  | CAN 1 离线 ID 25 | BOOL |  |  |  | X | X | X
报警 | 1041 | 9 | 301042 | 4 |  | CAN 1 离线 ID 26 | BOOL |  |  |  | X | X | X
报警 | 1041 | 10 | 301042 | 4 |  | CAN 1 离线 ID 27 | BOOL |  |  |  | X | X | X
报警 | 1041 | 11 | 301042 | 4 |  | CAN 1 离线 ID 28 | BOOL |  |  |  | X | X | X
报警 | 1041 | 12 | 301042 | 4 |  | CAN 1 离线 ID 29 | BOOL |  |  |  | X | X | X
报警 | 1041 | 13 | 301042 | 4 |  | CAN 1 离线 ID 30 | BOOL |  |  |  | X | X | X
报警 | 1041 | 14 | 301042 | 4 |  | CAN 1 离线 ID 31 | BOOL |  |  |  | X | X | X
报警 | 1041 | 15 | 301042 | 4 |  | CAN 1 离线 ID 32 | BOOL |  |  |  | X | X | X
报警 | 1042 | 0 | 301043 | 4 |  | CAN 1 离线 ID 33 | BOOL |  |  |  | X | X | X
报警 | 1042 | 1 | 301043 | 4 |  | CAN 1 离线 ID 34 | BOOL |  |  |  | X | X | X
报警 | 1042 | 2 | 301043 | 4 |  | CAN 1 离线 ID 35 | BOOL |  |  |  | X | X | X
报警 | 1042 | 3 | 301043 | 4 |  | CAN 1 离线 ID 36 | BOOL |  |  |  | X | X | X
报警 | 1042 | 4 | 301043 | 4 |  | CAN 1 离线 ID 37 | BOOL |  |  |  | X | X | X
报警 | 1042 | 5 | 301043 | 4 |  | CAN 1 离线 ID 38 | BOOL |  |  |  | X | X | X
报警 | 1042 | 6 | 301043 | 4 |  | CAN 1 离线 ID 39 | BOOL |  |  |  | X | X | X
报警 | 1042 | 7 | 301043 | 4 |  | CAN 1 离线 ID 40 | BOOL |  |  |  | X | X | X
报警 | 1043 | 0 | 301044 | 4 |  | CAN 2离线ID 1 | BOOL |  |  |  | X | X | X
报警 | 1043 | 1 | 301044 | 4 |  | CAN 2离线D 2 | BOOL |  |  |  | X | X | X
报警 | 1043 | 2 | 301044 | 4 |  | CAN 2离线ID 3 | BOOL |  |  |  | X | X | X
报警 | 1043 | 3 | 301044 | 4 |  | CAN 2离线ID 4 | BOOL |  |  |  | X | X | X
报警 | 1043 | 4 | 301044 | 4 |  | CAN 2离线ID 5 | BOOL |  |  |  | X | X | X
报警 | 1043 | 5 | 301044 | 4 |  | CAN 2离线ID 6 | BOOL |  |  |  | X | X | X
报警 | 1043 | 6 | 301044 | 4 |  | CAN 2离线ID 7 | BOOL |  |  |  | X | X | X
报警 | 1043 | 7 | 301044 | 4 |  | CAN 2离线ID 8 | BOOL |  |  |  | X | X | X
报警 | 1043 | 8 | 301044 | 4 |  | CAN 2离线ID 9 | BOOL |  |  |  | X | X | X
报警 | 1043 | 9 | 301044 | 4 |  | CAN 2离线ID 10 | BOOL |  |  |  | X | X | X
报警 | 1043 | 10 | 301044 | 4 |  | CAN 2离线ID 11 | BOOL |  |  |  | X | X | X
报警 | 1043 | 11 | 301044 | 4 |  | CAN 2离线ID 12 | BOOL |  |  |  | X | X | X
报警 | 1043 | 12 | 301044 | 4 |  | CAN 2离线ID 13 | BOOL |  |  |  | X | X | X
报警 | 1043 | 13 | 301044 | 4 |  | CAN 2离线ID 14 | BOOL |  |  |  | X | X | X
报警 | 1043 | 14 | 301044 | 4 |  | CAN 2离线ID 15 | BOOL |  |  |  | X | X | X
报警 | 1043 | 15 | 301044 | 4 |  | CAN 2离线ID 16 | BOOL |  |  |  | X | X | X
报警 | 1044 | 0 | 301045 | 4 |  | CAN 2离线ID 17 | BOOL |  |  |  | X | X | X
报警 | 1044 | 1 | 301045 | 4 |  | CAN 2离线ID 18 | BOOL |  |  |  | X | X | X
报警 | 1044 | 2 | 301045 | 4 |  | CAN 2离线ID 19 | BOOL |  |  |  | X | X | X
报警 | 1044 | 3 | 301045 | 4 |  | CAN 2离线ID 20 | BOOL |  |  |  | X | X | X
报警 | 1044 | 4 | 301045 | 4 |  | CAN 2离线ID 21 | BOOL |  |  |  | X | X | X
报警 | 1044 | 5 | 301045 | 4 |  | CAN 2离线ID 22 | BOOL |  |  |  | X | X | X
报警 | 1044 | 6 | 301045 | 4 |  | CAN 2离线ID 23 | BOOL |  |  |  | X | X | X
报警 | 1044 | 7 | 301045 | 4 |  | CAN 2离线ID 24 | BOOL |  |  |  | X | X | X
报警 | 1044 | 8 | 301045 | 4 |  | CAN 2离线ID 25 | BOOL |  |  |  | X | X | X
报警 | 1044 | 9 | 301045 | 4 |  | CAN 2离线ID 26 | BOOL |  |  |  | X | X | X
报警 | 1044 | 10 | 301045 | 4 |  | CAN 2离线ID 27 | BOOL |  |  |  | X | X | X
报警 | 1044 | 11 | 301045 | 4 |  | CAN 2离线ID 28 | BOOL |  |  |  | X | X | X
报警 | 1044 | 12 | 301045 | 4 |  | CAN 2离线ID 29 | BOOL |  |  |  | X | X | X
报警 | 1044 | 13 | 301045 | 4 |  | CAN 2离线ID 30 | BOOL |  |  |  | X | X | X
报警 | 1044 | 14 | 301045 | 4 |  | CAN 2离线ID 31 | BOOL |  |  |  | X | X | X
报警 | 1044 | 15 | 301045 | 4 |  | CAN 2离线ID 32 | BOOL |  |  |  | X | X | X
报警 | 1045 | 0 | 301046 | 4 |  | CAN 2离线ID 33 | BOOL |  |  |  | X | X | X
报警 | 1045 | 1 | 301046 | 4 |  | CAN 2离线ID 34 | BOOL |  |  |  | X | X | X
报警 | 1045 | 2 | 301046 | 4 |  | CAN 2离线ID 35 | BOOL |  |  |  | X | X | X
报警 | 1045 | 3 | 301046 | 4 |  | CAN 2离线ID 36 | BOOL |  |  |  | X | X | X
报警 | 1045 | 4 | 301046 | 4 |  | CAN 2离线ID 37 | BOOL |  |  |  | X | X | X
报警 | 1045 | 5 | 301046 | 4 |  | CAN 2离线ID 38 | BOOL |  |  |  | X | X | X
报警 | 1045 | 6 | 301046 | 4 |  | CAN 2离线ID 39 | BOOL |  |  |  | X | X | X
报警 | 1045 | 7 | 301046 | 4 |  | CAN 2离线ID 40 | BOOL |  |  |  | X | X | X
报警 | 1050 | 0 | 301051 | 4 |  | 准备就绪为自动启动 | BOOL | [5 empty] | X
报警 | 1050 | 1 | 301051 | 4 |  | 机组端电压小于30%额定值 | BOOL | [5 empty] | X
报警 | 1050 | 1 | 301051 | 4 |  | BA电压不低于30%Ue | BOOL |  |  |  | X
报警 | 1050 | 1 | 301051 | 4 |  | 主网(市电)电压不低于30%Ue | BOOL |  |  |  |  | X
报警 | 1050 | 2 | 301051 | 4 |  | 母排A端电压不小于30%额定值 | BOOL | [5 empty] | X
报警 | 1050 | 2 | 301051 | 4 |  | 母排电压不低于30%Ue | BOOL |  |  |  | X | X
报警 | 1051 |  | 301052 | 4 |  | 虚拟事件 1-16 | INT16s | AB | 0 |  | X | X | X
报警 | 1052 |  | 301053 | 4 |  | 虚拟事件 17-32 | INT16s | AB | 0 |  | X | X | X
报警 | 1053 | 0 | 301054 | 4 | 6590 | 风扇 A 故障 | BOOL | [5 empty] | X
报警 | 1053 | 1 | 301054 | 4 | 6600 | 风扇 B 故障 | BOOL | [5 empty] | X
报警 | 1053 | 2 | 301054 | 4 | 6610 | 风扇 C故障 | BOOL | [5 empty] | X
报警 | 1053 | 3 | 301054 | 4 | 6620 | 风扇 D 故障 | BOOL | [5 empty] | X
报警 | 1053 | 4 | 301054 | 4 | 4610 | Delta模拟量 1 - 故障 1 | BOOL |  |  |  | X | X | X
报警 | 1053 | 5 | 301054 | 4 | 4620 | Delta模拟量 1 - 故障 2 | BOOL |  |  |  | X | X | X
报警 | 1053 | 6 | 301054 | 4 | 4630 | Delta模拟量 2 - 故障 1 | BOOL |  |  |  | X | X | X
报警 | 1053 | 7 | 301054 | 4 | 4640 | Delta模拟量 2 - 故障 2 | BOOL |  |  |  | X | X | X
报警 | 1053 | 8 | 301054 | 4 | 4650 | Delta模拟量 3 - 故障 1 | BOOL |  |  |  | X | X | X
报警 | 1053 | 9 | 301054 | 4 | 4660 | Delta模拟量 3 - 故障 2 | BOOL |  |  |  | X | X | X
报警 | 1053 | 10 | 301054 | 4 | 4680 | Delta模拟量 4 - 故障 1 | BOOL |  |  |  | X | X | X
报警 | 1053 | 11 | 301054 | 4 | 4690 | Delta模拟量 4 - 故障 2 | BOOL |  |  |  | X | X | X
报警 | 1053 | 12 | 301054 | 4 | 4700 | Delta模拟量 5 - 故障 1 | BOOL |  |  |  | X | X | X
报警 | 1053 | 13 | 301054 | 4 | 4710 | Delta模拟量 5 - 故障 2 | BOOL |  |  |  | X | X | X
报警 | 1053 | 14 | 301054 | 4 | 4720 | Delta模拟量 6 - 故障 1 | BOOL |  |  |  | X | X | X
报警 | 1053 | 15 | 301054 | 4 | 4730 | Delta模拟量 6 - 故障2 | BOOL |  |  |  | X | X | X
报警 | 1054 | 0 | 301055 | 4 |  | 反时限过电流 | BOOL |  |  |  | X | X | X
报警 | 1054 | 1 | 301055 | 4 |  | 极端反时限过电流 | BOOL |  |  |  | X | X | X
报警 | 1054 | 3 | 301055 | 4 | 6352 | 机组外部停机 | BOOL | [5 empty] | X
报警 | 1054 | 4 | 301055 | 4 | 1710 | 机组不平衡电流2 | BOOL |  |  |  | X | X | X
报警 | 1054 | 5 | 301055 | 4 | 7480 | 母排(平均)过电压 1 | BOOL |  |  |  |  | X | X
报警 | 1054 | 6 | 301055 | 4 | 7490 | 母排(平均)过电压 2 | BOOL |  |  |  |  | X | X
报警 | 1054 | 7 | 301055 | 4 | 7440 | 第四相CT逆功 1 | BOOL |  |  |  | X | X | X
报警 | 1054 | 8 | 301055 | 4 | 7450 | 第四相CT逆功 2 | BOOL |  |  |  | X | X | X
报警 | 1054 | 9 | 301055 | 4 | 7460 | 第四相CT过载 1 | BOOL |  |  |  | X | X | X
报警 | 1054 | 10 | 301055 | 4 | 7470 | 第四相CT过载 2 | BOOL |  |  |  | X | X | X
报警 | 1055 | 0 | 301056 | 4 |  | LED 1 红色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 1 | 301056 | 4 |  | LED 1 黄色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 2 | 301056 | 4 |  | LED 1 绿色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 3 | 301056 | 4 |  | LED 1 闪烁 | BOOL |  |  |  | X | X | X
报警 | 1055 | 4 | 301056 | 4 |  | LED 2 红色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 5 | 301056 | 4 |  | LED 2 黄色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 6 | 301056 | 4 |  | LED 2 绿色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 7 | 301056 | 4 |  | LED 2 闪烁 | BOOL |  |  |  | X | X | X
报警 | 1055 | 8 | 301056 | 4 |  | LED 3 红色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 9 | 301056 | 4 |  | LED 3 黄色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 10 | 301056 | 4 |  | LED 3 绿色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 11 | 301056 | 4 |  | LED 3 闪烁 | BOOL |  |  |  | X | X | X
报警 | 1055 | 12 | 301056 | 4 |  | LED 4 红色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 13 | 301056 | 4 |  | LED 4 黄色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 14 | 301056 | 4 |  | LED 4 绿色 | BOOL |  |  |  | X | X | X
报警 | 1055 | 15 | 301056 | 4 |  | LED 4 闪烁 | BOOL |  |  |  | X | X | X
报警 | 1056 | 0 | 301057 | 4 | 7830 | DAVR通信失败 | BOOL | [5 empty] | X
报警 | 1056 | 1 | 301057 | 4 | 7761 | DAVR 报警 | BOOL | [5 empty] | X
报警 | 1056 | 2 | 301057 | 4 | 7763 | DAVR 跳闸 | BOOL | [5 empty] | X
报警 | 1057 | 0 | 301058 | 4 |  | 报警激活阻止起动+ 断路器合闸 | BOOL |  |  |  | X | X | X
报警 | 1057 | 1 | 301058 | 4 |  | 报警激活报警 | BOOL |  |  |  | X | X | X
报警 | 1057 | 2 | 301058 | 4 |  | 报警激活断开GB/TB/BTB | BOOL |  |  |  | X | X | X
报警 | 1057 | 3 | 301058 | 4 |  | 报警激活断开GB，冷却停机 | BOOL |  |  |  | X | X | X
报警 | 1057 | 4 | 301058 | 4 |  | 报警激活断开GB，立即停机 | BOOL |  |  |  | X | X | X
报警 | 1057 | 5 | 301058 | 4 |  | 报警激活分闸 MB | BOOL |  |  |  | X | X | X
报警 | 1057 | 6 | 301058 | 4 |  | 报警激活安全停机 | BOOL |  |  |  | X | X | X
报警 | 1057 | 7 | 301058 | 4 |  | 报警激活跳闸MB+GB（Trip MB+GB） | BOOL |  |  |  | X | X | X
报警 | 1057 | 8 | 301058 | 4 |  | 报警激活受控停机 (解列+ 冷却停机) | BOOL |  |  |  | X | X | X
PM AC 测量 | 1500 |  | 301501 | 4 |  | 总计功率 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1501 |  | 301502 | 4 |  | 储备功率 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1502 |  | 301503 | 4 |  | 总计额定功率 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1503 |  | 301504 | 4 |  | 总计 机组set 功率 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1504 |  | 301505 | 4 |  | 总计 无功功率 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1505 |  | 301506 | 4 |  | 机组总数（in application） | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1506 |  | 301507 | 4 |  | 电站类型(Plant type) | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1507 |  | 301508 | 4 |  | PM停机，有功设定点 | INT16s | AB | 0 |  |  |  | X
PM AC 测量 | 1508 |  | 301509 | 4 |  | PM起机，有功设定点 | INT16s | AB | 0 |  |  |  | X
PM AC 测量 | 1510 |  | 301511 | 4 |  | 额定功率 ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1511 |  | 301512 | 4 |  | 额定功率 ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1512 |  | 301513 | 4 |  | 额定功率 ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1513 |  | 301514 | 4 |  | 额定功率 ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1514 |  | 301515 | 4 |  | 额定功率 ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1515 |  | 301516 | 4 |  | 额定功率 ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1516 |  | 301517 | 4 |  | 额定功率 ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1517 |  | 301518 | 4 |  | 额定功率 ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1518 |  | 301519 | 4 |  | 额定功率 ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1519 |  | 301520 | 4 |  | 额定功率 ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1520 |  | 301521 | 4 |  | 额定功率 ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1521 |  | 301522 | 4 |  | 额定功率 ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1522 |  | 301523 | 4 |  | 额定功率 ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1523 |  | 301524 | 4 |  | 额定功率 ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1524 |  | 301525 | 4 |  | 额定功率 ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1525 |  | 301526 | 4 |  | 额定功率 ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1526 |  | 301527 | 4 |  | 有功功率ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1527 |  | 301528 | 4 |  | 有功功率ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1528 |  | 301529 | 4 |  | 有功功率ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1529 |  | 301530 | 4 |  | 有功功率ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1530 |  | 301531 | 4 |  | 有功功率ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1531 |  | 301532 | 4 |  | 有功功率ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1532 |  | 301533 | 4 |  | 有功功率ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1533 |  | 301534 | 4 |  | 有功功率ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1534 |  | 301535 | 4 |  | 有功功率ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1535 |  | 301536 | 4 |  | 有功功率ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1536 |  | 301537 | 4 |  | 有功功率ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1537 |  | 301538 | 4 |  | 有功功率ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1538 |  | 301539 | 4 |  | 有功功率ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1539 |  | 301540 | 4 |  | 有功功率ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1540 |  | 301541 | 4 |  | 有功功率ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1541 |  | 301542 | 4 |  | 有功功率ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1542 |  | 301543 | 4 |  | 无功功率 ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1543 |  | 301544 | 4 |  | 无功功率 ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1544 |  | 301545 | 4 |  | 无功功率 ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1545 |  | 301546 | 4 |  | 无功功率 ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1546 |  | 301547 | 4 |  | 无功功率 ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1547 |  | 301548 | 4 |  | 无功功率 ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1548 |  | 301549 | 4 |  | 无功功率 ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1549 |  | 301550 | 4 |  | 无功功率 ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1550 |  | 301551 | 4 |  | 无功功率 ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1551 |  | 301552 | 4 |  | 无功功率 ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1552 |  | 301553 | 4 |  | 无功功率 ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1553 |  | 301554 | 4 |  | 无功功率 ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1554 |  | 301555 | 4 |  | 无功功率 ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1555 |  | 301556 | 4 |  | 无功功率 ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1556 |  | 301557 | 4 |  | 无功功率 ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1557 |  | 301558 | 4 |  | 无功功率 ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1558 |  | 301559 | 4 |  | 机组优先级 | INT16s | AB | 0 |  |  |  | X
PM AC 测量 | 1560 |  | 301561 | 4 |  | 功率, 主网(市电) 1A | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1561 |  | 301562 | 4 |  | 功率, 主网(市电) 1B | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1562 |  | 301563 | 4 |  | 功率, 主网(市电) 2A | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1563 |  | 301564 | 4 |  | 功率, 主网(市电) 2B | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1565 |  | 301566 | 4 |  | 无功功率 主网(市电) 1A | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1566 |  | 301567 | 4 |  | 无功功率 主网(市电) 1B | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1567 |  | 301568 | 4 |  | 无功功率 主网(市电) 2A | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1568 |  | 301569 | 4 |  | 无功功率 主网(市电) 2B | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1569 |  | 301570 | 4 |  | 有功功率ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1570 |  | 301571 | 4 |  | 有功功率ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1571 |  | 301572 | 4 |  | 有功功率ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1572 |  | 301573 | 4 |  | 有功功率ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1573 |  | 301574 | 4 |  | 有功功率ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1574 |  | 301575 | 4 |  | 有功功率ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1575 |  | 301576 | 4 |  | 有功功率ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1576 |  | 301577 | 4 |  | 有功功率ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1577 |  | 301578 | 4 |  | 有功功率ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1578 |  | 301579 | 4 |  | 有功功率ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1579 |  | 301580 | 4 |  | 有功功率ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1580 |  | 301581 | 4 |  | 有功功率ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1581 |  | 301582 | 4 |  | 有功功率ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1582 |  | 301583 | 4 |  | 有功功率ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1583 |  | 301584 | 4 |  | 有功功率ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1584 |  | 301585 | 4 |  | 有功功率ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1585 |  | 301586 | 4 |  | 无功功率 ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1586 |  | 301587 | 4 |  | 无功功率 ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1587 |  | 301588 | 4 |  | 无功功率 ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1588 |  | 301589 | 4 |  | 无功功率 ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1589 |  | 301590 | 4 |  | 无功功率 ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1590 |  | 301591 | 4 |  | 无功功率 ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1591 |  | 301592 | 4 |  | 无功功率 ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1592 |  | 301593 | 4 |  | 无功功率 ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1593 |  | 301594 | 4 |  | 无功功率 ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1594 |  | 301595 | 4 |  | 无功功率 ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1595 |  | 301596 | 4 |  | 无功功率 ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1596 |  | 301597 | 4 |  | 无功功率 ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1597 |  | 301598 | 4 |  | 无功功率 ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1598 |  | 301599 | 4 |  | 无功功率 ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1599 |  | 301600 | 4 |  | 无功功率 ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1600 |  | 301601 | 4 |  | 无功功率 ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1601 |  | 301602 | 4 |  | 有功功率ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1602 |  | 301603 | 4 |  | 有功功率ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1603 |  | 301604 | 4 |  | 有功功率ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1604 |  | 301605 | 4 |  | 有功功率ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1605 |  | 301606 | 4 |  | 有功功率ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1606 |  | 301607 | 4 |  | 有功功率ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1607 |  | 301608 | 4 |  | 有功功率ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1608 |  | 301609 | 4 |  | 有功功率ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1609 |  | 301610 | 4 |  | 无功功率 ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1610 |  | 301611 | 4 |  | 无功功率 ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1611 |  | 301612 | 4 |  | 无功功率 ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1612 |  | 301613 | 4 |  | 无功功率 ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1613 |  | 301614 | 4 |  | 无功功率 ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1614 |  | 301615 | 4 |  | 无功功率 ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1615 |  | 301616 | 4 |  | 无功功率 ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1616 |  | 301617 | 4 |  | 无功功率 ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1617 |  | 301618 | 4 |  | 电站模式 (Plant mode) 主网(市电) 17 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1618 |  | 301619 | 4 |  | 电站模式 (Plant mode) 主网(市电) 18 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1619 |  | 301620 | 4 |  | 电站模式 (Plant mode) 主网(市电) 19 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1620 |  | 301621 | 4 |  | 电站模式 (Plant mode) 主网(市电) 20 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1621 |  | 301622 | 4 |  | 电站模式 (Plant mode) 主网(市电) 21 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1622 |  | 301623 | 4 |  | 电站模式 (Plant mode) 主网(市电) 22 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1623 |  | 301624 | 4 |  | 电站模式 (Plant mode) 主网(市电) 23 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1624 |  | 301625 | 4 |  | 电站模式 (Plant mode) 主网(市电) 24 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1625 |  | 301626 | 4 |  | 电站模式 (Plant mode) 主网(市电) 25 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1626 |  | 301627 | 4 |  | 电站模式 (Plant mode) 主网(市电) 26 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1627 |  | 301628 | 4 |  | 电站模式 (Plant mode) 主网(市电) 27 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1628 |  | 301629 | 4 |  | 电站模式 (Plant mode) 主网(市电) 28 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1629 |  | 301630 | 4 |  | 电站模式 (Plant mode) 主网(市电) 29 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1630 |  | 301631 | 4 |  | 电站模式 (Plant mode) 主网(市电) 30 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1631 |  | 301632 | 4 |  | 电站模式 (Plant mode) 主网(市电) 31 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1632 |  | 301633 | 4 |  | 电站模式 (Plant mode) 主网(市电) 32 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1633 |  | 301634 | 4 |  | 母排(Bus)功率 主网(市电) 17 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1634 |  | 301635 | 4 |  | 母排(Bus)功率 主网(市电) 18 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1635 |  | 301636 | 4 |  | 母排(Bus)功率 主网(市电) 19 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1636 |  | 301637 | 4 |  | 母排(Bus)功率 主网(市电) 20 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1637 |  | 301638 | 4 |  | 母排(Bus)功率 主网(市电) 21 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1638 |  | 301639 | 4 |  | 母排(Bus)功率 主网(市电) 22 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1639 |  | 301640 | 4 |  | 母排(Bus)功率 主网(市电) 23 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1640 |  | 301641 | 4 |  | 母排(Bus)功率 主网(市电) 24 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1641 |  | 301642 | 4 |  | 母排(Bus)功率 主网(市电) 25 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1642 |  | 301643 | 4 |  | 母排(Bus)功率 主网(市电) 26 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1643 |  | 301644 | 4 |  | 母排(Bus)功率 主网(市电) 27 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1644 |  | 301645 | 4 |  | 母排(Bus)功率 主网(市电) 28 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1645 |  | 301646 | 4 |  | 母排(Bus)功率 主网(市电) 29 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1646 |  | 301647 | 4 |  | 母排(Bus)功率 主网(市电) 30 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1647 |  | 301648 | 4 |  | 母排(Bus)功率 主网(市电) 31 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1648 |  | 301649 | 4 |  | 母排(Bus)功率 主网(市电) 32 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1649 | 1 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 17 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 2 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 18 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 3 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 19 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 4 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 20 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 5 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 21 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 6 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 22 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 7 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 23 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 8 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 24 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 9 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 25 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 10 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 26 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 11 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 27 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 12 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 28 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 13 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 29 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 14 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 30 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 15 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 31 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1649 | 0 | 301650 | 4 |  | 主网(市电) 变送器-可配置，ID 32 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 1 | 301651 | 4 |  | TB 变送器-可配置，ID 17 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 2 | 301651 | 4 |  | TB 变送器-可配置，ID 18 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 3 | 301651 | 4 |  | TB 变送器-可配置，ID 19 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 4 | 301651 | 4 |  | TB 变送器-可配置，ID 20 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 5 | 301651 | 4 |  | TB 变送器-可配置，ID 21 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 6 | 301651 | 4 |  | TB 变送器-可配置，ID 22 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 7 | 301651 | 4 |  | TB 变送器-可配置，ID 23 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 8 | 301651 | 4 |  | TB 变送器-可配置，ID 24 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 9 | 301651 | 4 |  | TB 变送器-可配置，ID 25 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 10 | 301651 | 4 |  | TB 变送器-可配置，ID 26 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 11 | 301651 | 4 |  | TB 变送器-可配置，ID 27 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 12 | 301651 | 4 |  | TB 变送器-可配置，ID 28 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 13 | 301651 | 4 |  | TB 变送器-可配置，ID 29 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 14 | 301651 | 4 |  | TB 变送器-可配置，ID 30 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 15 | 301651 | 4 |  | TB 变送器-可配置，ID 31 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1650 | 0 | 301651 | 4 |  | TB 变送器-可配置，ID 32 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 1 | 301652 | 4 |  | BTB 变送器-可配置，ID 33 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 2 | 301652 | 4 |  | BTB 变送器-可配置，ID 34 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 3 | 301652 | 4 |  | BTB 变送器-可配置，ID 35 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 4 | 301652 | 4 |  | BTB 变送器-可配置，ID 36 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 5 | 301652 | 4 |  | BTB 变送器-可配置，ID 37 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 6 | 301652 | 4 |  | BTB 变送器-可配置，ID 38 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 7 | 301652 | 4 |  | BTB 变送器-可配置，ID 39 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1651 | 8 | 301652 | 4 |  | BTB 变送器-可配置，ID 40 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 1 | 301653 | 4 |  | ID 33 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 2 | 301653 | 4 |  | ID 34 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 3 | 301653 | 4 |  | ID 35 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 4 | 301653 | 4 |  | ID 36 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 5 | 301653 | 4 |  | ID 37 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 6 | 301653 | 4 |  | ID 38 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 7 | 301653 | 4 |  | ID 39 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1652 | 8 | 301653 | 4 |  | ID 40 BTB 被控制了 | BOOL |  |  |  | X | X | X
PM AC 测量 | 1653 |  | 301654 | 4 |  | 额定功率 ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1654 |  | 301655 | 4 |  | 额定功率 ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1655 |  | 301656 | 4 |  | 额定功率 ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1656 |  | 301657 | 4 |  | 额定功率 ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1657 |  | 301658 | 4 |  | 额定功率 ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1658 |  | 301659 | 4 |  | 额定功率 ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1659 |  | 301660 | 4 |  | 额定功率 ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1660 |  | 301661 | 4 |  | 额定功率 ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1661 |  | 301662 | 4 |  | 额定功率 ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1662 |  | 301663 | 4 |  | 额定功率 ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1663 |  | 301664 | 4 |  | 额定功率 ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1664 |  | 301665 | 4 |  | 额定功率 ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1665 |  | 301666 | 4 |  | 额定功率 ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1666 |  | 301667 | 4 |  | 额定功率 ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1667 |  | 301668 | 4 |  | 额定功率 ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC 测量 | 1668 |  | 301669 | 4 |  | 额定功率 ID 32 | INT16s | AB | 0 |  | X | X | X
PM报警 | 1700 | 0 | 301701 | 4 |  | TB储备功率 | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 1 | 301701 | 4 |  | 主网(市电) 储备功率 | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 2 | 301701 | 4 |  | 主网(市电）之一位置反馈ON | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 3 | 301701 | 4 |  | 所有主网(市电)位置反馈OFF | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 4 | 301701 | 4 |  | TB位置反馈ON（主网(市电) 单元） | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 5 | 301701 | 4 |  | TB位置反馈OFF（主网(市电) 单元） | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 6 | 301701 | 4 |  | GB之一位置反馈ON | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 7 | 301701 | 4 |  | 所有GB 位置反馈OFF | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 8 | 301701 | 4 |  | TB之一位置反馈ON | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 9 | 301701 | 4 |  | 所有TB 位置反馈OFF | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 10 | 301701 | 4 |  | BTB之一位置反馈ON | BOOL |  |  |  | X | X | X
PM报警 | 1700 | 11 | 301701 | 4 |  | BTB之一位置反馈OFF | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 1 | 301702 | 4 |  | GB 位置反馈ON ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 2 | 301702 | 4 |  | GB 位置反馈ON ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 3 | 301702 | 4 |  | GB 位置反馈ON ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 4 | 301702 | 4 |  | GB 位置反馈ON ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 5 | 301702 | 4 |  | GB 位置反馈ON ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 6 | 301702 | 4 |  | GB 位置反馈ON ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 7 | 301702 | 4 |  | GB 位置反馈ON ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 8 | 301702 | 4 |  | GB 位置反馈ON ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 9 | 301702 | 4 |  | GB 位置反馈ON ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 10 | 301702 | 4 |  | GB 位置反馈ON ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 11 | 301702 | 4 |  | GB 位置反馈ON ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 12 | 301702 | 4 |  | GB 位置反馈ON ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 13 | 301702 | 4 |  | GB 位置反馈ON ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 14 | 301702 | 4 |  | GB 位置反馈ON ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 15 | 301702 | 4 |  | GB 位置反馈ON ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1701 | 0 | 301702 | 4 |  | GB 位置反馈ON ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 1 | 301703 | 4 |  | GB 位置反馈OFF ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 2 | 301703 | 4 |  | GB 位置反馈OFF ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 3 | 301703 | 4 |  | GB 位置反馈OFF ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 4 | 301703 | 4 |  | GB 位置反馈OFF ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 5 | 301703 | 4 |  | GB 位置反馈OFF ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 6 | 301703 | 4 |  | GB 位置反馈OFF ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 7 | 301703 | 4 |  | GB 位置反馈OFF ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 8 | 301703 | 4 |  | GB 位置反馈OFF ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 9 | 301703 | 4 |  | GB 位置反馈OFF ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 10 | 301703 | 4 |  | GB 位置反馈OFF ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 11 | 301703 | 4 |  | GB 位置反馈OFF ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 12 | 301703 | 4 |  | GB 位置反馈OFF ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 13 | 301703 | 4 |  | GB 位置反馈OFF ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 14 | 301703 | 4 |  | GB 位置反馈OFF ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 15 | 301703 | 4 |  | GB 位置反馈OFF ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1702 | 0 | 301703 | 4 |  | GB 位置反馈OFF ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 1 | 301704 | 4 |  | DG 频率/电压 OK，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 2 | 301704 | 4 |  | DG 频率/电压 OK，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 3 | 301704 | 4 |  | DG 频率/电压 OK，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 4 | 301704 | 4 |  | DG 频率/电压 OK，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 5 | 301704 | 4 |  | DG 频率/电压 OK，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 6 | 301704 | 4 |  | DG 频率/电压 OK，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 7 | 301704 | 4 |  | DG 频率/电压 OK，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 8 | 301704 | 4 |  | DG 频率/电压 OK，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 9 | 301704 | 4 |  | DG 频率/电压 OK，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 10 | 301704 | 4 |  | DG 频率/电压 OK，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 11 | 301704 | 4 |  | DG 频率/电压 OK，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 12 | 301704 | 4 |  | DG 频率/电压 OK，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 13 | 301704 | 4 |  | DG 频率/电压 OK，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 14 | 301704 | 4 |  | DG 频率/电压 OK，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 15 | 301704 | 4 |  | DG 频率/电压 OK，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1703 | 0 | 301704 | 4 |  | DG 频率/电压 OK，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1704 | 0 | 301705 | 4 |  | 主网(市电) OK, 单一主网(市电) | BOOL |  |  |  | X | X | X
PM报警 | 1704 | 1 | 301705 | 4 |  | 主网(市电) OK, 主网(市电) 1A | BOOL |  |  |  | X | X | X
PM报警 | 1704 | 2 | 301705 | 4 |  | 主网(市电) OK, 主网(市电) 1B | BOOL |  |  |  | X | X | X
PM报警 | 1704 | 3 | 301705 | 4 |  | 主网(市电) OK, 主网(市电) 2A | BOOL |  |  |  | X | X | X
PM报警 | 1704 | 4 | 301705 | 4 |  | 主网(市电) OK, 主网(市电) 2B | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 1 | 301706 | 4 |  | 自动启动准备就绪，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 2 | 301706 | 4 |  | 自动启动准备就绪，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 3 | 301706 | 4 |  | 自动启动准备就绪，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 4 | 301706 | 4 |  | 自动启动准备就绪，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 5 | 301706 | 4 |  | 自动启动准备就绪，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 6 | 301706 | 4 |  | 自动启动准备就绪，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 7 | 301706 | 4 |  | 自动启动准备就绪，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 8 | 301706 | 4 |  | 自动启动准备就绪，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 9 | 301706 | 4 |  | 自动启动准备就绪，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 10 | 301706 | 4 |  | 自动启动准备就绪，ID10 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 11 | 301706 | 4 |  | 自动启动准备就绪，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 12 | 301706 | 4 |  | 自动启动准备就绪，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 13 | 301706 | 4 |  | 自动启动准备就绪，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 14 | 301706 | 4 |  | 自动启动准备就绪，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 15 | 301706 | 4 |  | 自动启动准备就绪，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1705 | 0 | 301706 | 4 |  | 自动启动准备就绪，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1706 | 0 | 301707 | 4 |  | 主网(市电)不在半自动, 单一主网(市电) | BOOL |  |  |  | X | X | X
PM报警 | 1706 | 1 | 301707 | 4 |  | 主网(市电)不在半自动, 主网(市电)1A | BOOL |  |  |  | X | X | X
PM报警 | 1706 | 2 | 301707 | 4 |  | 主网(市电)不在半自动, 主网(市电) 1B | BOOL |  |  |  | X | X | X
PM报警 | 1706 | 3 | 301707 | 4 |  | 主网(市电)不在半自动, 主网(市电) 2A | BOOL |  |  |  | X | X | X
PM报警 | 1706 | 4 | 301707 | 4 |  | 电主网(市电)不在半自动, 主网(市电) 2B | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 1 | 301708 | 4 |  | 报警之一存在，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 2 | 301708 | 4 |  | 报警之一存在，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 3 | 301708 | 4 |  | 报警之一存在，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 4 | 301708 | 4 |  | 报警之一存在，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 5 | 301708 | 4 |  | 报警之一存在，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 6 | 301708 | 4 |  | 报警之一存在，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 7 | 301708 | 4 |  | 报警之一存在，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 8 | 301708 | 4 |  | 报警之一存在，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 9 | 301708 | 4 |  | 报警之一存在，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 10 | 301708 | 4 |  | 报警之一存在，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 11 | 301708 | 4 |  | 报警之一存在，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 12 | 301708 | 4 |  | 报警之一存在，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 13 | 301708 | 4 |  | 报警之一存在，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 14 | 301708 | 4 |  | 报警之一存在，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 15 | 301708 | 4 |  | 报警之一存在，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1707 | 0 | 301708 | 4 |  | 报警之一存在，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1708 | 0 | 301709 | 4 |  | 报警之一存在，单一主网(市电) | BOOL |  |  |  | X | X | X
PM报警 | 1708 | 1 | 301709 | 4 |  | 报警之一存在，主网(市电) 1A | BOOL |  |  |  | X | X | X
PM报警 | 1708 | 2 | 301709 | 4 |  | 报警之一存在，主网(市电) 1B | BOOL |  |  |  | X | X | X
PM报警 | 1708 | 3 | 301709 | 4 |  | 报警之一存在，主网(市电) 2A | BOOL |  |  |  | X | X | X
PM报警 | 1708 | 4 | 301709 | 4 |  | 报警之一存在，主网(市电) 2B | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 1 | 301710 | 4 |  | 机组运行, ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 2 | 301710 | 4 |  | 机组运行, ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 3 | 301710 | 4 |  | 机组运行, ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 4 | 301710 | 4 |  | 机组运行, ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 5 | 301710 | 4 |  | 机组运行, ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 6 | 301710 | 4 |  | 机组运行, ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 7 | 301710 | 4 |  | 机组运行, ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 8 | 301710 | 4 |  | 机组运行, ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 9 | 301710 | 4 |  | 机组运行, ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 10 | 301710 | 4 |  | 机组运行, ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 11 | 301710 | 4 |  | 机组运行, ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 12 | 301710 | 4 |  | 机组运行, ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 13 | 301710 | 4 |  | 机组运行, ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 14 | 301710 | 4 |  | 机组运行, ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 15 | 301710 | 4 |  | 机组运行, ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1709 | 0 | 301710 | 4 |  | 机组运行, ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 0 | 301711 | 4 |  | MB 位置反馈ON，单一主网(市电) | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 1 | 301711 | 4 |  | MB 位置反馈ON，主网(市电) 1A | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 2 | 301711 | 4 |  | MB 位置反馈ON，主网(市电) 1B | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 3 | 301711 | 4 |  | MB 位置反馈ON，主网(市电) 2A | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 4 | 301711 | 4 |  | MB 位置反馈ON，主网(市电) 2B | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 5 | 301711 | 4 |  | MB 位置反馈OFF，单一主网(市电) | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 6 | 301711 | 4 |  | MB 位置反馈OFF，主网(市电) 1A | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 7 | 301711 | 4 |  | MB 位置反馈OFF，主网(市电) 1B | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 8 | 301711 | 4 |  | MB 位置反馈OFF，主网(市电) 2A | BOOL |  |  |  | X | X | X
PM报警 | 1710 | 9 | 301711 | 4 |  | MB 位置反馈OFF，主网(市电) 2B | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 1 | 301712 | 4 |  | GB 正在同步, ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 2 | 301712 | 4 |  | GB 正在同步, ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 3 | 301712 | 4 |  | GB 正在同步, ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 4 | 301712 | 4 |  | GB 正在同步, ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 5 | 301712 | 4 |  | GB 正在同步, ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 6 | 301712 | 4 |  | GB 正在同步, ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 7 | 301712 | 4 |  | GB 正在同步, ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 8 | 301712 | 4 |  | GB 正在同步, ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 9 | 301712 | 4 |  | GB 正在同步, ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 10 | 301712 | 4 |  | GB 正在同步, ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 11 | 301712 | 4 |  | GB 正在同步, ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 12 | 301712 | 4 |  | GB 正在同步, ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 13 | 301712 | 4 |  | GB 正在同步, ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 14 | 301712 | 4 |  | GB 正在同步, ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 15 | 301712 | 4 |  | GB 正在同步, ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1711 | 0 | 301712 | 4 |  | GB 正在同步, ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 1 | 301713 | 4 |  | 主网(市电) OK，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 2 | 301713 | 4 |  | 主网(市电) OK，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 3 | 301713 | 4 |  | 主网(市电) OK，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 4 | 301713 | 4 |  | 主网(市电) OK，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 5 | 301713 | 4 |  | 主网(市电) OK，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 6 | 301713 | 4 |  | 主网(市电) OK，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 7 | 301713 | 4 |  | 主网(市电) OK，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 8 | 301713 | 4 |  | 主网(市电) OK，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 9 | 301713 | 4 |  | 主网(市电) OK，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 10 | 301713 | 4 |  | 主网(市电) OK，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 11 | 301713 | 4 |  | 主网(市电) OK，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 12 | 301713 | 4 |  | 主网(市电) OK，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 13 | 301713 | 4 |  | 主网(市电) OK，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 14 | 301713 | 4 |  | 主网(市电) OK，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 15 | 301713 | 4 |  | 主网(市电) OK，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1712 | 0 | 301713 | 4 |  | 主网(市电) OK，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 1 | 301714 | 4 |  | 主网(市电)不在半自动 17 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 2 | 301714 | 4 |  | 主网(市电)不在半自动 18 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 3 | 301714 | 4 |  | 主网(市电)不在半自动 19 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 4 | 301714 | 4 |  | 主网(市电)不在半自动 20 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 5 | 301714 | 4 |  | 主网(市电)不在半自动 21 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 6 | 301714 | 4 |  | 主网(市电)不在半自动 22 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 7 | 301714 | 4 |  | 主网(市电)不在半自动 23 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 8 | 301714 | 4 |  | 主网(市电)不在半自动 24 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 9 | 301714 | 4 |  | 主网(市电)不在半自动 25 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 10 | 301714 | 4 |  | 主网(市电)不在半自动 26 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 11 | 301714 | 4 |  | 主网(市电)不在半自动 27 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 12 | 301714 | 4 |  | 主网(市电)不在半自动 28 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 13 | 301714 | 4 |  | 主网(市电)不在半自动 29 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 14 | 301714 | 4 |  | 主网(市电)不在半自动 30 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 15 | 301714 | 4 |  | 主网(市电)不在半自动 31 | BOOL |  |  |  | X | X | X
PM报警 | 1713 | 0 | 301714 | 4 |  | 主网(市电)不在半自动 32 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 1 | 301715 | 4 |  | 报警之一存在，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 2 | 301715 | 4 |  | 报警之一存在，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 3 | 301715 | 4 |  | 报警之一存在，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 4 | 301715 | 4 |  | 报警之一存在，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 5 | 301715 | 4 |  | 报警之一存在，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 6 | 301715 | 4 |  | 报警之一存在，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 7 | 301715 | 4 |  | 报警之一存在，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 8 | 301715 | 4 |  | 报警之一存在，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 9 | 301715 | 4 |  | 报警之一存在，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 10 | 301715 | 4 |  | 报警之一存在，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 11 | 301715 | 4 |  | 报警之一存在，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 12 | 301715 | 4 |  | 报警之一存在，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 13 | 301715 | 4 |  | 报警之一存在，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 14 | 301715 | 4 |  | 报警之一存在，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 15 | 301715 | 4 |  | 报警之一存在，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1714 | 0 | 301715 | 4 |  | 报警之一存在，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 1 | 301716 | 4 |  | MB 位置反馈ON，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 2 | 301716 | 4 |  | MB 位置反馈ON，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 3 | 301716 | 4 |  | MB 位置反馈ON，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 4 | 301716 | 4 |  | MB 位置反馈ON，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 5 | 301716 | 4 |  | MB 位置反馈ON，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 6 | 301716 | 4 |  | MB 位置反馈ON，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 7 | 301716 | 4 |  | MB 位置反馈ON，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 8 | 301716 | 4 |  | MB 位置反馈ON，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 9 | 301716 | 4 |  | MB 位置反馈ON，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 10 | 301716 | 4 |  | MB 位置反馈ON，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 11 | 301716 | 4 |  | MB 位置反馈ON，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 12 | 301716 | 4 |  | MB 位置反馈ON，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 13 | 301716 | 4 |  | MB 位置反馈ON，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 14 | 301716 | 4 |  | MB 位置反馈ON，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 15 | 301716 | 4 |  | MB 位置反馈ON，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1715 | 0 | 301716 | 4 |  | MB 位置反馈ON，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 1 | 301717 | 4 |  | MB 位置反馈OFF，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 2 | 301717 | 4 |  | MB 位置反馈OFF，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 3 | 301717 | 4 |  | MB 位置反馈OFF，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 4 | 301717 | 4 |  | MB 位置反馈OFF，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 5 | 301717 | 4 |  | MB 位置反馈OFF，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 6 | 301717 | 4 |  | MB 位置反馈OFF，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 7 | 301717 | 4 |  | MB 位置反馈OFF，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 8 | 301717 | 4 |  | MB 位置反馈OFF，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 9 | 301717 | 4 |  | MB 位置反馈OFF，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 10 | 301717 | 4 |  | MB 位置反馈OFF，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 11 | 301717 | 4 |  | MB 位置反馈OFF，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 12 | 301717 | 4 |  | MB 位置反馈OFF，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 13 | 301717 | 4 |  | MB 位置反馈OFF，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 14 | 301717 | 4 |  | MB 位置反馈OFF，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 15 | 301717 | 4 |  | MB 位置反馈OFF，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1716 | 0 | 301717 | 4 |  | MB 位置反馈OFF，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 1 | 301718 | 4 |  | 主网(市电)故障, ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 2 | 301718 | 4 |  | 主网(市电)故障, ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 3 | 301718 | 4 |  | 主网(市电)故障, ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 4 | 301718 | 4 |  | 主网(市电)故障, ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 5 | 301718 | 4 |  | 主网(市电)故障, ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 6 | 301718 | 4 |  | 主网(市电)故障, ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 7 | 301718 | 4 |  | 主网(市电)故障, ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 8 | 301718 | 4 |  | 主网(市电)故障, ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 9 | 301718 | 4 |  | 主网(市电)故障, ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 10 | 301718 | 4 |  | 主网(市电)故障, ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 11 | 301718 | 4 |  | 主网(市电)故障, ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 12 | 301718 | 4 |  | 主网(市电)故障, ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 13 | 301718 | 4 |  | 主网(市电)故障, ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 14 | 301718 | 4 |  | 主网(市电)故障, ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 15 | 301718 | 4 |  | 主网(市电)故障, ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1717 | 0 | 301718 | 4 |  | 主网(市电)故障, ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 1 | 301719 | 4 |  | MB 正在同步, ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 2 | 301719 | 4 |  | MB 正在同步, ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 3 | 301719 | 4 |  | MB 正在同步, ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 4 | 301719 | 4 |  | MB 正在同步, ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 5 | 301719 | 4 |  | MB 正在同步, ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 6 | 301719 | 4 |  | MB 正在同步, ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 7 | 301719 | 4 |  | MB 正在同步, ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 8 | 301719 | 4 |  | MB 正在同步, ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 9 | 301719 | 4 |  | MB 正在同步, ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 10 | 301719 | 4 |  | MB 正在同步, ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 11 | 301719 | 4 |  | MB 正在同步, ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 12 | 301719 | 4 |  | MB 正在同步, ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 13 | 301719 | 4 |  | MB 正在同步, ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 14 | 301719 | 4 |  | MB 正在同步, ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 15 | 301719 | 4 |  | MB 正在同步, ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1718 | 0 | 301719 | 4 |  | MB 正在同步, ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 1 | 301720 | 4 |  | TB位置反馈ON，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 2 | 301720 | 4 |  | TB位置反馈ON，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 3 | 301720 | 4 |  | TB位置反馈ON，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 4 | 301720 | 4 |  | TB位置反馈ON，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 5 | 301720 | 4 |  | TB位置反馈ON，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 6 | 301720 | 4 |  | TB位置反馈ON，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 7 | 301720 | 4 |  | TB位置反馈ON，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 8 | 301720 | 4 |  | TB位置反馈ON，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 9 | 301720 | 4 |  | TB位置反馈ON，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 10 | 301720 | 4 |  | TB位置反馈ON，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 11 | 301720 | 4 |  | TB位置反馈ON，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 12 | 301720 | 4 |  | TB位置反馈ON，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 13 | 301720 | 4 |  | TB位置反馈ON，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 14 | 301720 | 4 |  | TB位置反馈ON，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 15 | 301720 | 4 |  | TB位置反馈ON，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1719 | 0 | 301720 | 4 |  | TB位置反馈ON，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 1 | 301721 | 4 |  | TB位置反馈OFF，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 2 | 301721 | 4 |  | TB位置反馈OFF，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 3 | 301721 | 4 |  | TB位置反馈OFF，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 4 | 301721 | 4 |  | TB位置反馈OFF，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 5 | 301721 | 4 |  | TB位置反馈OFF，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 6 | 301721 | 4 |  | TB位置反馈OFF，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 7 | 301721 | 4 |  | TB位置反馈OFF，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 8 | 301721 | 4 |  | TB位置反馈OFF，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 9 | 301721 | 4 |  | TB位置反馈OFF，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 10 | 301721 | 4 |  | TB位置反馈OFF，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 11 | 301721 | 4 |  | TB位置反馈OFF，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 12 | 301721 | 4 |  | TB位置反馈OFF，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 13 | 301721 | 4 |  | TB位置反馈OFF，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 14 | 301721 | 4 |  | TB位置反馈OFF，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 15 | 301721 | 4 |  | TB位置反馈OFF，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1720 | 0 | 301721 | 4 |  | TB位置反馈OFF，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 1 | 301722 | 4 |  | TB 正在同步, ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 2 | 301722 | 4 |  | TB 正在同步, ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 3 | 301722 | 4 |  | TB 正在同步, ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 4 | 301722 | 4 |  | TB 正在同步, ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 5 | 301722 | 4 |  | TB 正在同步, ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 6 | 301722 | 4 |  | TB 正在同步, ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 7 | 301722 | 4 |  | TB 正在同步, ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 8 | 301722 | 4 |  | TB 正在同步, ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 9 | 301722 | 4 |  | TB 正在同步, ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 10 | 301722 | 4 |  | TB 正在同步, ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 11 | 301722 | 4 |  | TB 正在同步, ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 12 | 301722 | 4 |  | TB 正在同步, ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 13 | 301722 | 4 |  | TB 正在同步, ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 14 | 301722 | 4 |  | TB 正在同步, ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 15 | 301722 | 4 |  | TB 正在同步, ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1721 | 0 | 301722 | 4 |  | TB 正在同步, ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 1 | 301723 | 4 |  | 报警之一存在，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 2 | 301723 | 4 |  | 报警之一存在，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 3 | 301723 | 4 |  | 报警之一存在，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 4 | 301723 | 4 |  | 报警之一存在，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 5 | 301723 | 4 |  | 报警之一存在，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 6 | 301723 | 4 |  | 报警之一存在，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 7 | 301723 | 4 |  | 报警之一存在，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1722 | 8 | 301723 | 4 |  | 报警之一存在，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 1 | 301726 | 4 |  | BTB 正在同步, ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 2 | 301726 | 4 |  | BTB 正在同步, ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 3 | 301726 | 4 |  | BTB 正在同步, ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 4 | 301726 | 4 |  | BTB 正在同步, ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 5 | 301726 | 4 |  | BTB 正在同步, ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 6 | 301726 | 4 |  | BTB 正在同步, ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 7 | 301726 | 4 |  | BTB 正在同步, ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1725 | 8 | 301726 | 4 |  | BTB 正在同步, ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 1 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 2 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 3 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 4 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 5 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 6 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 7 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 8 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 9 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 10 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 11 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 12 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 13 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 14 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 15 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1727 | 0 | 301728 | 4 |  | 外部MODBUS通信出错，CAN ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 1 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 2 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 3 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 4 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 5 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 6 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 7 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1728 | 8 | 301729 | 4 |  | 外部MODBUS通信出错，CAN ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 1 | 301733 | 4 |  | 母排频率/电压OK，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 2 | 301733 | 4 |  | 母排频率/电压OK，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 3 | 301733 | 4 |  | 母排频率/电压OK，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 4 | 301733 | 4 |  | 母排频率/电压OK，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 5 | 301733 | 4 |  | 母排频率/电压OK，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 6 | 301733 | 4 |  | 母排频率/电压OK，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 7 | 301733 | 4 |  | 母排频率/电压OK，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 8 | 301733 | 4 |  | 母排频率/电压OK，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 9 | 301733 | 4 |  | 母排频率/电压OK，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 10 | 301733 | 4 |  | 母排频率/电压OK，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 11 | 301733 | 4 |  | 母排频率/电压OK，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 12 | 301733 | 4 |  | 母排频率/电压OK，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 13 | 301733 | 4 |  | 母排频率/电压OK，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 14 | 301733 | 4 |  | 母排频率/电压OK，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 15 | 301733 | 4 |  | 母排频率/电压OK，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1732 | 0 | 301733 | 4 |  | 母排频率/电压OK，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 1 | 301734 | 4 |  | 母排频率/电压OK，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 2 | 301734 | 4 |  | 母排频率/电压OK，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 3 | 301734 | 4 |  | 母排频率/电压OK，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 4 | 301734 | 4 |  | 母排频率/电压OK，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 5 | 301734 | 4 |  | 母排频率/电压OK，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 6 | 301734 | 4 |  | 母排频率/电压OK，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 7 | 301734 | 4 |  | 母排频率/电压OK，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 8 | 301734 | 4 |  | 母排频率/电压OK，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 9 | 301734 | 4 |  | 母排频率/电压OK，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 10 | 301734 | 4 |  | 母排频率/电压OK，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 11 | 301734 | 4 |  | 母排频率/电压OK，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 12 | 301734 | 4 |  | 母排频率/电压OK，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 13 | 301734 | 4 |  | 母排频率/电压OK，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 14 | 301734 | 4 |  | 母排频率/电压OK，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 15 | 301734 | 4 |  | 母排频率/电压OK，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1733 | 0 | 301734 | 4 |  | 母排频率/电压OK，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 1 | 301735 | 4 |  | 母排频率/电压OK，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 2 | 301735 | 4 |  | 母排频率/电压OK，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 3 | 301735 | 4 |  | 母排频率/电压OK，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 4 | 301735 | 4 |  | 母排频率/电压OK，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 5 | 301735 | 4 |  | 母排频率/电压OK，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 6 | 301735 | 4 |  | 母排频率/电压OK，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 7 | 301735 | 4 |  | 母排频率/电压OK，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1734 | 8 | 301735 | 4 |  | 母排频率/电压OK，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 1 | 301736 | 4 |  | 母排频率/电压存在，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 2 | 301736 | 4 |  | 母排频率/电压存在，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 3 | 301736 | 4 |  | 母排频率/电压存在，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 4 | 301736 | 4 |  | 母排频率/电压存在，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 5 | 301736 | 4 |  | 母排频率/电压存在，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 6 | 301736 | 4 |  | 母排频率/电压存在，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 7 | 301736 | 4 |  | 母排频率/电压存在，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 8 | 301736 | 4 |  | 母排频率/电压存在，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 9 | 301736 | 4 |  | 母排频率/电压存在，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 10 | 301736 | 4 |  | 母排频率/电压存在，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 11 | 301736 | 4 |  | 母排频率/电压存在，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 12 | 301736 | 4 |  | 母排频率/电压存在，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 13 | 301736 | 4 |  | 母排频率/电压存在，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 14 | 301736 | 4 |  | 母排频率/电压存在，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 15 | 301736 | 4 |  | 母排频率/电压存在，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1735 | 0 | 301736 | 4 |  | 母排频率/电压存在，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 1 | 301737 | 4 |  | 母排频率/电压存在，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 2 | 301737 | 4 |  | 母排频率/电压存在，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 3 | 301737 | 4 |  | 母排频率/电压存在，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 4 | 301737 | 4 |  | 母排频率/电压存在，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 5 | 301737 | 4 |  | 母排频率/电压存在，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 6 | 301737 | 4 |  | 母排频率/电压存在，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 7 | 301737 | 4 |  | 母排频率/电压存在，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 8 | 301737 | 4 |  | 母排频率/电压存在，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 9 | 301737 | 4 |  | 母排频率/电压存在，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 10 | 301737 | 4 |  | 母排频率/电压存在，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 11 | 301737 | 4 |  | 母排频率/电压存在，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 12 | 301737 | 4 |  | 母排频率/电压存在，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 13 | 301737 | 4 |  | 母排频率/电压存在，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 14 | 301737 | 4 |  | 母排频率/电压存在，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 15 | 301737 | 4 |  | 母排频率/电压存在，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1736 | 0 | 301737 | 4 |  | 母排频率/电压存在，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 1 | 301738 | 4 |  | 母排频率/电压存在，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 2 | 301738 | 4 |  | 母排频率/电压存在，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 3 | 301738 | 4 |  | 母排频率/电压存在，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 4 | 301738 | 4 |  | 母排频率/电压存在，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 5 | 301738 | 4 |  | 母排频率/电压存在，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 6 | 301738 | 4 |  | 母排频率/电压存在，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 7 | 301738 | 4 |  | 母排频率/电压存在，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1737 | 8 | 301738 | 4 |  | 母排频率/电压存在，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 1 | 301739 | 4 |  | BA频率/电压OK，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 2 | 301739 | 4 |  | BA频率/电压OK，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 3 | 301739 | 4 |  | BA频率/电压OK，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 4 | 301739 | 4 |  | BA频率/电压OK，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 5 | 301739 | 4 |  | BA频率/电压OK，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 6 | 301739 | 4 |  | BA频率/电压OK，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 7 | 301739 | 4 |  | BA频率/电压OK，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1738 | 8 | 301739 | 4 |  | BA频率/电压OK，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 1 | 301740 | 4 |  | DG 频率/电压存在，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 2 | 301740 | 4 |  | DG 频率/电压存在，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 3 | 301740 | 4 |  | DG 频率/电压存在，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 4 | 301740 | 4 |  | DG 频率/电压存在，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 5 | 301740 | 4 |  | DG 频率/电压存在，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 6 | 301740 | 4 |  | DG 频率/电压存在，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 7 | 301740 | 4 |  | DG 频率/电压存在，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 8 | 301740 | 4 |  | DG 频率/电压存在，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 9 | 301740 | 4 |  | DG 频率/电压存在，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 10 | 301740 | 4 |  | DG 频率/电压存在，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 11 | 301740 | 4 |  | DG 频率/电压存在，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 12 | 301740 | 4 |  | DG 频率/电压存在，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 13 | 301740 | 4 |  | DG 频率/电压存在，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 14 | 301740 | 4 |  | DG 频率/电压存在，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 15 | 301740 | 4 |  | DG 频率/电压存在，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1739 | 0 | 301740 | 4 |  | DG 频率/电压存在，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 1 | 301741 | 4 |  | 频率/电压存在，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 2 | 301741 | 4 |  | 频率/电压存在，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 3 | 301741 | 4 |  | 频率/电压存在，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 4 | 301741 | 4 |  | 频率/电压存在，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 5 | 301741 | 4 |  | 频率/电压存在，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 6 | 301741 | 4 |  | 频率/电压存在，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 7 | 301741 | 4 |  | 频率/电压存在，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 8 | 301741 | 4 |  | 频率/电压存在，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 9 | 301741 | 4 |  | 频率/电压存在，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 10 | 301741 | 4 |  | 频率/电压存在，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 11 | 301741 | 4 |  | 频率/电压存在，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 12 | 301741 | 4 |  | 频率/电压存在，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 13 | 301741 | 4 |  | 频率/电压存在，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 14 | 301741 | 4 |  | 频率/电压存在，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 15 | 301741 | 4 |  | 频率/电压存在，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1740 | 0 | 301741 | 4 |  | 频率/电压存在，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 1 | 301742 | 4 |  | BA 频率/电压存在，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 2 | 301742 | 4 |  | BA 频率/电压存在，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 3 | 301742 | 4 |  | BA 频率/电压存在，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 4 | 301742 | 4 |  | BA 频率/电压存在，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 5 | 301742 | 4 |  | BA 频率/电压存在，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 6 | 301742 | 4 |  | BA 频率/电压存在，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 7 | 301742 | 4 |  | BA 频率/电压存在，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1741 | 8 | 301742 | 4 |  | BA 频率/电压存在，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 1 | 301744 | 4 |  | 冗余备份存在 ID1 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 2 | 301744 | 4 |  | 冗余备份存在 ID2 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 3 | 301744 | 4 |  | 冗余备份存在 ID3 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 4 | 301744 | 4 |  | 冗余备份存在 ID4 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 5 | 301744 | 4 |  | 冗余备份存在 ID5 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 6 | 301744 | 4 |  | 冗余备份存在 ID6 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 7 | 301744 | 4 |  | 冗余备份存在 ID7 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 8 | 301744 | 4 |  | 冗余备份存在 ID8 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 9 | 301744 | 4 |  | 冗余备份存在 ID9 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 10 | 301744 | 4 |  | 冗余备份存在 ID10 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 11 | 301744 | 4 |  | 冗余备份存在 ID11 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 12 | 301744 | 4 |  | 冗余备份存在 ID12 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 13 | 301744 | 4 |  | 冗余备份存在 ID13 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 14 | 301744 | 4 |  | 冗余备份存在 ID14 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 15 | 301744 | 4 |  | 冗余备份存在 ID15 | BOOL |  |  |  | X | X | X
PM报警 | 1743 | 0 | 301744 | 4 |  | 冗余备份存在 ID16 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 1 | 301745 | 4 |  | 冗余备份存在 ID17 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 2 | 301745 | 4 |  | 冗余备份存在 ID18 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 3 | 301745 | 4 |  | 冗余备份存在 ID19 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 4 | 301745 | 4 |  | 冗余备份存在 ID20 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 5 | 301745 | 4 |  | 冗余备份存在 ID21 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 6 | 301745 | 4 |  | 冗余备份存在 ID22 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 7 | 301745 | 4 |  | 冗余备份存在 ID23 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 8 | 301745 | 4 |  | 冗余备份存在 ID24 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 9 | 301745 | 4 |  | 冗余备份存在 ID25 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 10 | 301745 | 4 |  | 冗余备份存在 ID26 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 11 | 301745 | 4 |  | 冗余备份存在 ID27 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 12 | 301745 | 4 |  | 冗余备份存在 ID28 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 13 | 301745 | 4 |  | 冗余备份存在 ID29 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 14 | 301745 | 4 |  | 冗余备份存在 ID30 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 15 | 301745 | 4 |  | 冗余备份存在 ID31 | BOOL |  |  |  | X | X | X
PM报警 | 1744 | 0 | 301745 | 4 |  | 冗余备份存在 ID32 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 1 | 301746 | 4 |  | 冗余备份存在 ID33 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 2 | 301746 | 4 |  | 冗余备份存在 ID34 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 3 | 301746 | 4 |  | 冗余备份存在 ID35 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 4 | 301746 | 4 |  | 冗余备份存在 ID36 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 5 | 301746 | 4 |  | 冗余备份存在 ID37 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 6 | 301746 | 4 |  | 冗余备份存在 ID38 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 7 | 301746 | 4 |  | 冗余备份存在 ID39 | BOOL |  |  |  | X | X | X
PM报警 | 1745 | 8 | 301746 | 4 |  | 冗余备份存在 ID40 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 1 | 301747 | 4 |  | 控制器 B 激活在 ID1 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 2 | 301747 | 4 |  | 控制器 B 激活在 ID2 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 3 | 301747 | 4 |  | 控制器 B 激活在 ID3 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 4 | 301747 | 4 |  | 控制器 B 激活在 ID4 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 5 | 301747 | 4 |  | 控制器 B 激活在 ID5 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 6 | 301747 | 4 |  | 控制器 B 激活在 ID6 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 7 | 301747 | 4 |  | 控制器 B 激活在 ID7 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 8 | 301747 | 4 |  | 控制器 B 激活在 ID8 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 9 | 301747 | 4 |  | 控制器 B 激活在 ID9 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 10 | 301747 | 4 |  | 控制器 B 激活在 ID10 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 11 | 301747 | 4 |  | 控制器 B 激活在 ID11 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 12 | 301747 | 4 |  | 控制器 B 激活在 ID12 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 13 | 301747 | 4 |  | 控制器 B 激活在 ID13 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 14 | 301747 | 4 |  | 控制器 B 激活在 ID14 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 15 | 301747 | 4 |  | 控制器 B 激活在 ID15 | BOOL |  |  |  | X | X | X
PM报警 | 1746 | 0 | 301747 | 4 |  | 控制器 B 激活在 ID16 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 1 | 301748 | 4 |  | 控制器 B 激活在 ID17 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 2 | 301748 | 4 |  | 控制器 B 激活在 ID18 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 3 | 301748 | 4 |  | 控制器 B 激活在 ID19 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 4 | 301748 | 4 |  | 控制器 B 激活在 ID20 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 5 | 301748 | 4 |  | 控制器 B 激活在 ID21 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 6 | 301748 | 4 |  | 控制器 B 激活在 ID22 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 7 | 301748 | 4 |  | 控制器 B 激活在 ID23 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 8 | 301748 | 4 |  | 控制器 B 激活在 ID24 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 9 | 301748 | 4 |  | 控制器 B 激活在 ID25 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 10 | 301748 | 4 |  | 控制器 B 激活在 ID26 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 11 | 301748 | 4 |  | 控制器 B 激活在 ID27 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 12 | 301748 | 4 |  | 控制器 B 激活在 ID28 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 13 | 301748 | 4 |  | 控制器 B 激活在 ID29 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 14 | 301748 | 4 |  | 控制器 B 激活在 ID30 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 15 | 301748 | 4 |  | 控制器 B 激活在 ID31 | BOOL |  |  |  | X | X | X
PM报警 | 1747 | 0 | 301748 | 4 |  | 控制器 B 激活在 ID32 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 1 | 301749 | 4 |  | 控制器 B 激活在 ID33 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 2 | 301749 | 4 |  | 控制器 B 激活在 ID34 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 3 | 301749 | 4 |  | 控制器 B 激活在 ID35 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 4 | 301749 | 4 |  | 控制器 B 激活在 ID36 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 5 | 301749 | 4 |  | 控制器 B 激活在 ID37 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 6 | 301749 | 4 |  | 控制器 B 激活在 ID38 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 7 | 301749 | 4 |  | 控制器 B 激活在 ID39 | BOOL |  |  |  | X | X | X
PM报警 | 1748 | 8 | 301749 | 4 |  | 控制器 B 激活在 ID40 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 1 | 301750 | 4 |  | 烘干模式激活在 ID1 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 2 | 301750 | 4 |  | 烘干模式激活在 ID2 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 3 | 301750 | 4 |  | 烘干模式激活在 ID3 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 4 | 301750 | 4 |  | 烘干模式激活在 ID4 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 5 | 301750 | 4 |  | 烘干模式激活在 ID5 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 6 | 301750 | 4 |  | 烘干模式激活在 ID6 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 7 | 301750 | 4 |  | 烘干模式激活在 ID7 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 8 | 301750 | 4 |  | 烘干模式激活在 ID8 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 9 | 301750 | 4 |  | 烘干模式激活在 ID9 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 10 | 301750 | 4 |  | 烘干模式激活在 ID10 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 11 | 301750 | 4 |  | 烘干模式激活在 ID11 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 12 | 301750 | 4 |  | 烘干模式激活在 ID12 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 13 | 301750 | 4 |  | 烘干模式激活在 ID13 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 14 | 301750 | 4 |  | 烘干模式激活在 ID14 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 15 | 301750 | 4 |  | 烘干模式激活在 ID15 | BOOL |  |  |  | X | X | X
PM报警 | 1749 | 0 | 301750 | 4 |  | 烘干模式激活在 ID16 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 1 | 301751 | 4 |  | GB 位置反馈 ON，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 2 | 301751 | 4 |  | GB 位置反馈 ON，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 3 | 301751 | 4 |  | GB 位置反馈 ON，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 4 | 301751 | 4 |  | GB 位置反馈 ON，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 5 | 301751 | 4 |  | GB 位置反馈 ON，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 6 | 301751 | 4 |  | GB 位置反馈 ON，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 7 | 301751 | 4 |  | GB 位置反馈 ON，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 8 | 301751 | 4 |  | GB 位置反馈 ON，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 9 | 301751 | 4 |  | GB 位置反馈 ON，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 10 | 301751 | 4 |  | GB 位置反馈 ON，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 11 | 301751 | 4 |  | GB 位置反馈 ON，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 12 | 301751 | 4 |  | GB 位置反馈 ON，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 13 | 301751 | 4 |  | GB 位置反馈 ON，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 14 | 301751 | 4 |  | GB 位置反馈 ON，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 15 | 301751 | 4 |  | GB 位置反馈 ON，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1750 | 0 | 301751 | 4 |  | GB 位置反馈 ON，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 1 | 301752 | 4 |  | GB 位置反馈 OFF，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 2 | 301752 | 4 |  | GB 位置反馈 OFF，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 3 | 301752 | 4 |  | GB 位置反馈 OFF，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 4 | 301752 | 4 |  | GB 位置反馈 OFF，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 5 | 301752 | 4 |  | GB 位置反馈 OFF，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 6 | 301752 | 4 |  | GB 位置反馈 OFF，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 7 | 301752 | 4 |  | GB 位置反馈 OFF，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 8 | 301752 | 4 |  | GB 位置反馈 OFF，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 9 | 301752 | 4 |  | GB 位置反馈 OFF，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 10 | 301752 | 4 |  | GB 位置反馈 OFF，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 11 | 301752 | 4 |  | GB 位置反馈 OFF，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 12 | 301752 | 4 |  | GB 位置反馈 OFF，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 13 | 301752 | 4 |  | GB 位置反馈 OFF，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 14 | 301752 | 4 |  | GB 位置反馈 OFF，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 15 | 301752 | 4 |  | GB 位置反馈 OFF，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1751 | 0 | 301752 | 4 |  | GB 位置反馈 OFF，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 1 | 301753 | 4 |  | GB 正在同步, ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 2 | 301753 | 4 |  | GB 正在同步, ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 3 | 301753 | 4 |  | GB 正在同步, ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 4 | 301753 | 4 |  | GB 正在同步, ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 5 | 301753 | 4 |  | GB 正在同步, ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 6 | 301753 | 4 |  | GB 正在同步, ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 7 | 301753 | 4 |  | GB 正在同步, ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 8 | 301753 | 4 |  | GB 正在同步, ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 9 | 301753 | 4 |  | GB 正在同步, ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 10 | 301753 | 4 |  | GB 正在同步, ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 11 | 301753 | 4 |  | GB 正在同步, ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 12 | 301753 | 4 |  | GB 正在同步, ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 13 | 301753 | 4 |  | GB 正在同步, ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 14 | 301753 | 4 |  | GB 正在同步, ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 15 | 301753 | 4 |  | GB 正在同步, ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1752 | 0 | 301753 | 4 |  | GB 正在同步, ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 1 | 301754 | 4 |  | 频率/电压 OK, ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 2 | 301754 | 4 |  | 频率/电压 OK, ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 3 | 301754 | 4 |  | 频率/电压 OK, ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 4 | 301754 | 4 |  | 频率/电压 OK, ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 5 | 301754 | 4 |  | 频率/电压 OK, ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 6 | 301754 | 4 |  | 频率/电压 OK, ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 7 | 301754 | 4 |  | 频率/电压 OK, ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 8 | 301754 | 4 |  | 频率/电压 OK, ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 9 | 301754 | 4 |  | 频率/电压 OK, ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 10 | 301754 | 4 |  | 频率/电压 OK, ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 11 | 301754 | 4 |  | 频率/电压 OK, ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 12 | 301754 | 4 |  | 频率/电压 OK, ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 13 | 301754 | 4 |  | 频率/电压 OK, ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 14 | 301754 | 4 |  | 频率/电压 OK, ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 15 | 301754 | 4 |  | 频率/电压 OK, ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1753 | 0 | 301754 | 4 |  | 频率/电压 OK, ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 1 | 301755 | 4 |  | 自动启动准备就绪，ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 2 | 301755 | 4 |  | 自动启动准备就绪，ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 3 | 301755 | 4 |  | 自动启动准备就绪，ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 4 | 301755 | 4 |  | 自动启动准备就绪，ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 5 | 301755 | 4 |  | 自动启动准备就绪，ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 6 | 301755 | 4 |  | 自动启动准备就绪，ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 7 | 301755 | 4 |  | 自动启动准备就绪，ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 8 | 301755 | 4 |  | 自动启动准备就绪，ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 9 | 301755 | 4 |  | 自动启动准备就绪，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 10 | 301755 | 4 |  | 自动启动准备就绪，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 11 | 301755 | 4 |  | 自动启动准备就绪，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 12 | 301755 | 4 |  | 自动启动准备就绪，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 13 | 301755 | 4 |  | 自动启动准备就绪，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 14 | 301755 | 4 |  | 自动启动准备就绪，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 15 | 301755 | 4 |  | 自动启动准备就绪，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1754 | 0 | 301755 | 4 |  | 自动启动准备就绪，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 1 | 301756 | 4 |  | 运行, ID 17 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 2 | 301756 | 4 |  | 运行, ID 18 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 3 | 301756 | 4 |  | 运行, ID 19 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 4 | 301756 | 4 |  | 运行, ID 20 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 5 | 301756 | 4 |  | 运行, ID 21 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 6 | 301756 | 4 |  | 运行, ID 22 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 7 | 301756 | 4 |  | 运行, ID 23 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 8 | 301756 | 4 |  | 运行, ID 24 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 9 | 301756 | 4 |  | 运行, ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 10 | 301756 | 4 |  | 运行, ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 11 | 301756 | 4 |  | 运行, ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 12 | 301756 | 4 |  | 运行, ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 13 | 301756 | 4 |  | 运行, ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 14 | 301756 | 4 |  | 运行, ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 15 | 301756 | 4 |  | 运行, ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1755 | 0 | 301756 | 4 |  | 运行, ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 1 | 301757 | 4 |  | 烘干模式激活在 ID17 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 2 | 301757 | 4 |  | 烘干模式激活在 ID18 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 3 | 301757 | 4 |  | 烘干模式激活在 ID19 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 4 | 301757 | 4 |  | 烘干模式激活在 ID20 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 5 | 301757 | 4 |  | 烘干模式激活在 ID21 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 6 | 301757 | 4 |  | 烘干模式激活在 ID22 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 7 | 301757 | 4 |  | 烘干模式激活在 ID23 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 8 | 301757 | 4 |  | 烘干模式激活在 ID24 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 9 | 301757 | 4 |  | 烘干模式激活在 ID25 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 10 | 301757 | 4 |  | 烘干模式激活在 ID26 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 11 | 301757 | 4 |  | 烘干模式激活在 ID27 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 12 | 301757 | 4 |  | 烘干模式激活在 ID28 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 13 | 301757 | 4 |  | 烘干模式激活在 ID29 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 14 | 301757 | 4 |  | 烘干模式激活在 ID30 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 15 | 301757 | 4 |  | 烘干模式激活在 ID31 | BOOL |  |  |  | X | X | X
PM报警 | 1756 | 0 | 301757 | 4 |  | 烘干模式激活在 ID32 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 1 | 301758 | 4 |  | MB 位置反馈ON，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 2 | 301758 | 4 |  | MB 位置反馈ON，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 3 | 301758 | 4 |  | MB 位置反馈ON，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 4 | 301758 | 4 |  | MB 位置反馈ON，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 5 | 301758 | 4 |  | MB 位置反馈ON，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 6 | 301758 | 4 |  | MB 位置反馈ON，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 7 | 301758 | 4 |  | MB 位置反馈ON，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 8 | 301758 | 4 |  | MB 位置反馈ON，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 9 | 301758 | 4 |  | MB 位置反馈ON，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 10 | 301758 | 4 |  | MB 位置反馈ON，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 11 | 301758 | 4 |  | MB 位置反馈ON，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 12 | 301758 | 4 |  | MB 位置反馈ON，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 13 | 301758 | 4 |  | MB 位置反馈ON，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 14 | 301758 | 4 |  | MB 位置反馈ON，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 15 | 301758 | 4 |  | MB 位置反馈ON，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1757 | 0 | 301758 | 4 |  | MB 位置反馈ON，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 1 | 301759 | 4 |  | MB 位置反馈OFF，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 2 | 301759 | 4 |  | MB 位置反馈OFF，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 3 | 301759 | 4 |  | MB 位置反馈OFF，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 4 | 301759 | 4 |  | MB 位置反馈OFF，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 5 | 301759 | 4 |  | MB 位置反馈OFF，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 6 | 301759 | 4 |  | MB 位置反馈OFF，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 7 | 301759 | 4 |  | MB 位置反馈OFF，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 8 | 301759 | 4 |  | MB 位置反馈OFF，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 9 | 301759 | 4 |  | MB 位置反馈OFF，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 10 | 301759 | 4 |  | MB 位置反馈OFF，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 11 | 301759 | 4 |  | MB 位置反馈OFF，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 12 | 301759 | 4 |  | MB 位置反馈OFF，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 13 | 301759 | 4 |  | MB 位置反馈OFF，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 14 | 301759 | 4 |  | MB 位置反馈OFF，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 15 | 301759 | 4 |  | MB 位置反馈OFF，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1758 | 0 | 301759 | 4 |  | MB 位置反馈OFF，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 1 | 301760 | 4 |  | MB 正在同步, ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 2 | 301760 | 4 |  | MB 正在同步, ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 3 | 301760 | 4 |  | MB 正在同步, ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 4 | 301760 | 4 |  | MB 正在同步, ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 5 | 301760 | 4 |  | MB 正在同步, ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 6 | 301760 | 4 |  | MB 正在同步, ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 7 | 301760 | 4 |  | MB 正在同步, ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 8 | 301760 | 4 |  | MB 正在同步, ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 9 | 301760 | 4 |  | MB 正在同步, ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 10 | 301760 | 4 |  | MB 正在同步, ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 11 | 301760 | 4 |  | MB 正在同步, ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 12 | 301760 | 4 |  | MB 正在同步, ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 13 | 301760 | 4 |  | MB 正在同步, ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 14 | 301760 | 4 |  | MB 正在同步, ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 15 | 301760 | 4 |  | MB 正在同步, ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1759 | 0 | 301760 | 4 |  | MB 正在同步, ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 1 | 301761 | 4 |  | TB位置反馈ON，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 2 | 301761 | 4 |  | TB位置反馈ON，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 3 | 301761 | 4 |  | TB位置反馈ON，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 4 | 301761 | 4 |  | TB位置反馈ON，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 5 | 301761 | 4 |  | TB位置反馈ON，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 6 | 301761 | 4 |  | TB位置反馈ON，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 7 | 301761 | 4 |  | TB位置反馈ON，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 8 | 301761 | 4 |  | TB位置反馈ON，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 9 | 301761 | 4 |  | TB位置反馈ON，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 10 | 301761 | 4 |  | TB位置反馈ON，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 11 | 301761 | 4 |  | TB位置反馈ON，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 12 | 301761 | 4 |  | TB位置反馈ON，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 13 | 301761 | 4 |  | TB位置反馈ON，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 14 | 301761 | 4 |  | TB位置反馈ON，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 15 | 301761 | 4 |  | TB位置反馈ON，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1760 | 0 | 301761 | 4 |  | TB位置反馈ON，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 1 | 301762 | 4 |  | TB位置反馈OFF，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 2 | 301762 | 4 |  | TB位置反馈OFF，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 3 | 301762 | 4 |  | TB位置反馈OFF，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 4 | 301762 | 4 |  | TB位置反馈OFF，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 5 | 301762 | 4 |  | TB位置反馈OFF，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 6 | 301762 | 4 |  | TB位置反馈OFF，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 7 | 301762 | 4 |  | TB位置反馈OFF，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 8 | 301762 | 4 |  | TB位置反馈OFF，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 9 | 301762 | 4 |  | TB位置反馈OFF，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 10 | 301762 | 4 |  | TB位置反馈OFF，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 11 | 301762 | 4 |  | TB位置反馈OFF，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 12 | 301762 | 4 |  | TB位置反馈OFF，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 13 | 301762 | 4 |  | TB位置反馈OFF，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 14 | 301762 | 4 |  | TB位置反馈OFF，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 15 | 301762 | 4 |  | TB位置反馈OFF，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1761 | 0 | 301762 | 4 |  | TB位置反馈OFF，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 1 | 301763 | 4 |  | TB 正在同步, ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 2 | 301763 | 4 |  | TB 正在同步, ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 3 | 301763 | 4 |  | TB 正在同步, ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 4 | 301763 | 4 |  | TB 正在同步, ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 5 | 301763 | 4 |  | TB 正在同步, ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 6 | 301763 | 4 |  | TB 正在同步, ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 7 | 301763 | 4 |  | TB 正在同步, ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 8 | 301763 | 4 |  | TB 正在同步, ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 9 | 301763 | 4 |  | TB 正在同步, ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 10 | 301763 | 4 |  | TB 正在同步, ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 11 | 301763 | 4 |  | TB 正在同步, ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 12 | 301763 | 4 |  | TB 正在同步, ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 13 | 301763 | 4 |  | TB 正在同步, ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 14 | 301763 | 4 |  | TB 正在同步, ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 15 | 301763 | 4 |  | TB 正在同步, ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1762 | 0 | 301763 | 4 |  | TB 正在同步, ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 1 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 2 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 3 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 4 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 5 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 6 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 7 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 8 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 9 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 10 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 11 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 12 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 13 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 14 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 15 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1763 | 0 | 301764 | 4 |  | 主网(市电) 变送器-可配置，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 1 | 301765 | 4 |  | TB 变送器-可配置，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 2 | 301765 | 4 |  | TB 变送器-可配置，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 3 | 301765 | 4 |  | TB 变送器-可配置，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 4 | 301765 | 4 |  | TB 变送器-可配置，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 5 | 301765 | 4 |  | TB 变送器-可配置，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 6 | 301765 | 4 |  | TB 变送器-可配置，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 7 | 301765 | 4 |  | TB 变送器-可配置，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 8 | 301765 | 4 |  | TB 变送器-可配置，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 9 | 301765 | 4 |  | TB 变送器-可配置，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 10 | 301765 | 4 |  | TB 变送器-可配置，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 11 | 301765 | 4 |  | TB 变送器-可配置，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 12 | 301765 | 4 |  | TB 变送器-可配置，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 13 | 301765 | 4 |  | TB 变送器-可配置，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 14 | 301765 | 4 |  | TB 变送器-可配置，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 15 | 301765 | 4 |  | TB 变送器-可配置，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1764 | 0 | 301765 | 4 |  | TB 变送器-可配置，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 1 | 301766 | 4 |  | 主网(市电) OK，ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 2 | 301766 | 4 |  | 主网(市电) OK，ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 3 | 301766 | 4 |  | 主网(市电) OK，ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 4 | 301766 | 4 |  | 主网(市电) OK，ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 5 | 301766 | 4 |  | 主网(市电) OK，ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 6 | 301766 | 4 |  | 主网(市电) OK，ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 7 | 301766 | 4 |  | 主网(市电) OK，ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 8 | 301766 | 4 |  | 主网(市电) OK，ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 9 | 301766 | 4 |  | 主网(市电) OK，ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 10 | 301766 | 4 |  | 主网(市电) OK，ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 11 | 301766 | 4 |  | 主网(市电) OK，ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 12 | 301766 | 4 |  | 主网(市电) OK，ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 13 | 301766 | 4 |  | 主网(市电) OK，ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 14 | 301766 | 4 |  | 主网(市电) OK，ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 15 | 301766 | 4 |  | 主网(市电) OK，ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1765 | 0 | 301766 | 4 |  | 主网(市电) OK，ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 1 | 301767 | 4 |  | 主网(市电)不在半自动 1 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 2 | 301767 | 4 |  | 主网(市电)不在半自动 2 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 3 | 301767 | 4 |  | 主网(市电)不在半自动 3 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 4 | 301767 | 4 |  | 主网(市电)不在半自动 4 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 5 | 301767 | 4 |  | 主网(市电)不在半自动 5 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 6 | 301767 | 4 |  | 主网(市电)不在半自动 6 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 7 | 301767 | 4 |  | 主网(市电)不在半自动 7 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 8 | 301767 | 4 |  | 主网(市电)不在半自动 8 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 9 | 301767 | 4 |  | 主网(市电)不在半自动 9 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 10 | 301767 | 4 |  | 主网(市电)不在半自动 10 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 11 | 301767 | 4 |  | 主网(市电)不在半自动 11 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 12 | 301767 | 4 |  | 主网(市电)不在半自动 12 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 13 | 301767 | 4 |  | 主网(市电)不在半自动 13 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 14 | 301767 | 4 |  | 主网(市电)不在半自动 14 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 15 | 301767 | 4 |  | 主网(市电)不在半自动 15 | BOOL |  |  |  | X | X | X
PM报警 | 1766 | 0 | 301767 | 4 |  | 主网(市电)不在半自动 16 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 1 | 301768 | 4 |  | 主网(市电)故障, ID 1 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 2 | 301768 | 4 |  | 主网(市电)故障, ID 2 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 3 | 301768 | 4 |  | 主网(市电)故障, ID 3 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 4 | 301768 | 4 |  | 主网(市电)故障, ID 4 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 5 | 301768 | 4 |  | 主网(市电)故障, ID 5 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 6 | 301768 | 4 |  | 主网(市电)故障, ID 6 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 7 | 301768 | 4 |  | 主网(市电)故障, ID 7 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 8 | 301768 | 4 |  | 主网(市电)故障, ID 8 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 9 | 301768 | 4 |  | 主网(市电)故障, ID 9 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 10 | 301768 | 4 |  | 主网(市电)故障, ID 10 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 11 | 301768 | 4 |  | 主网(市电)故障, ID 11 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 12 | 301768 | 4 |  | 主网(市电)故障, ID 12 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 13 | 301768 | 4 |  | 主网(市电)故障, ID 13 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 14 | 301768 | 4 |  | 主网(市电)故障, ID 14 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 15 | 301768 | 4 |  | 主网(市电)故障, ID 15 | BOOL |  |  |  | X | X | X
PM报警 | 1767 | 0 | 301768 | 4 |  | 主网(市电)故障, ID 16 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 1 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 2 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 3 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 4 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 5 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 6 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 7 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1770 | 8 | 301771 | 4 |  | 断路器 正在同步, 太阳能 ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 1 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 2 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 3 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 4 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 5 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 6 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 7 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 8 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 9 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 10 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 11 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 12 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 13 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 14 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 15 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 0 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1771 | 1 | 301772 | 4 |  | 太阳能 运行 / LG断路器之一闭合，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 1 | 301773 | 4 |  | 准备就绪为自动启动，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 2 | 301773 | 4 |  | 准备就绪为自动启动，ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 3 | 301773 | 4 |  | 准备就绪为自动启动，ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 4 | 301773 | 4 |  | 准备就绪为自动启动，ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 5 | 301773 | 4 |  | 准备就绪为自动启动，ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 6 | 301773 | 4 |  | 准备就绪为自动启动，ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 7 | 301773 | 4 |  | 准备就绪为自动启动，ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 8 | 301773 | 4 |  | 准备就绪为自动启动，ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 9 | 301773 | 4 |  | 准备就绪为自动启动，ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 10 | 301773 | 4 |  | 准备就绪为自动启动，ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 11 | 301773 | 4 |  | 准备就绪为自动启动，ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 12 | 301773 | 4 |  | 准备就绪为自动启动，ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 13 | 301773 | 4 |  | 准备就绪为自动启动，ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 14 | 301773 | 4 |  | 准备就绪为自动启动，ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 15 | 301773 | 4 |  | 准备就绪为自动启动，ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 0 | 301773 | 4 |  | 准备就绪为自动启动，ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1772 | 1 | 301773 | 4 |  | 准备就绪为自动启动，ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 1 | 301774 | 4 |  | 负载组1 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 2 | 301774 | 4 |  | 负载组 1 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 3 | 301774 | 4 |  | 负载组 1 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 4 | 301774 | 4 |  | 负载组 1 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 5 | 301774 | 4 |  | 负载组 1 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 6 | 301774 | 4 |  | 负载组 1 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 7 | 301774 | 4 |  | 负载组 1 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 8 | 301774 | 4 |  | 负载组 1 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 9 | 301774 | 4 |  | 负载组 1 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 10 | 301774 | 4 |  | 负载组 1 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 11 | 301774 | 4 |  | 负载组 1 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 12 | 301774 | 4 |  | 负载组 1 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 13 | 301774 | 4 |  | 负载组 1 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 14 | 301774 | 4 |  | 负载组 1 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 15 | 301774 | 4 |  | 负载组 1 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 0 | 301774 | 4 |  | 负载组 1 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1773 | 1 | 301774 | 4 |  | 负载组1 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 1 | 301775 | 4 |  | 负载组 2 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 2 | 301775 | 4 |  | 负载组 2 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 3 | 301775 | 4 |  | 负载组 2 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 4 | 301775 | 4 |  | 负载组 2 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 5 | 301775 | 4 |  | 负载组 2 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 6 | 301775 | 4 |  | 负载组 2 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 7 | 301775 | 4 |  | 负载组 2 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 8 | 301775 | 4 |  | 负载组 2 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 9 | 301775 | 4 |  | 负载组 2 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 10 | 301775 | 4 |  | 负载组 2 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 11 | 301775 | 4 |  | 负载组 2 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 12 | 301775 | 4 |  | 负载组 2 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 13 | 301775 | 4 |  | 负载组 2 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 14 | 301775 | 4 |  | 负载组 2 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 15 | 301775 | 4 |  | 负载组 2 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 0 | 301775 | 4 |  | 负载组 2 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1774 | 1 | 301775 | 4 |  | 负载组 2 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 1 | 301776 | 4 |  | 负载组 3 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 2 | 301776 | 4 |  | 负载组 3 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 3 | 301776 | 4 |  | 负载组 3 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 4 | 301776 | 4 |  | 负载组 3 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 5 | 301776 | 4 |  | 负载组 3 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 6 | 301776 | 4 |  | 负载组 3 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 7 | 301776 | 4 |  | 负载组 3 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 8 | 301776 | 4 |  | 负载组 3 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 9 | 301776 | 4 |  | 负载组 3 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 10 | 301776 | 4 |  | 负载组 3 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 11 | 301776 | 4 |  | 负载组 3 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 12 | 301776 | 4 |  | 负载组 3 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 13 | 301776 | 4 |  | 负载组 3 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 14 | 301776 | 4 |  | 负载组 3 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 15 | 301776 | 4 |  | 负载组 3 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 0 | 301776 | 4 |  | 负载组 3 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1775 | 1 | 301776 | 4 |  | 负载组 3 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 1 | 301777 | 4 |  | 负载组 4 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 2 | 301777 | 4 |  | 负载组 4 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 3 | 301777 | 4 |  | 负载组 4 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 4 | 301777 | 4 |  | 负载组 4 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 5 | 301777 | 4 |  | 负载组 4 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 6 | 301777 | 4 |  | 负载组 4 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 7 | 301777 | 4 |  | 负载组 4 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 8 | 301777 | 4 |  | 负载组 4 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 9 | 301777 | 4 |  | 负载组 4 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 10 | 301777 | 4 |  | 负载组 4 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 11 | 301777 | 4 |  | 负载组 4 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 12 | 301777 | 4 |  | 负载组 4 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 13 | 301777 | 4 |  | 负载组 4 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 14 | 301777 | 4 |  | 负载组 4 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 15 | 301777 | 4 |  | 负载组 4 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 0 | 301777 | 4 |  | 负载组 4 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1776 | 1 | 301777 | 4 |  | 负载组 4 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 1 | 301778 | 4 |  | 负载组 5 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 2 | 301778 | 4 |  | 负载组 5 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 3 | 301778 | 4 |  | 负载组 5 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 4 | 301778 | 4 |  | 负载组 5 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 5 | 301778 | 4 |  | 负载组 5 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 6 | 301778 | 4 |  | 负载组 5 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 7 | 301778 | 4 |  | 负载组 5 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 8 | 301778 | 4 |  | 负载组 5 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 9 | 301778 | 4 |  | 负载组 5 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 10 | 301778 | 4 |  | 负载组 5 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 11 | 301778 | 4 |  | 负载组 5 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 12 | 301778 | 4 |  | 负载组 5 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 13 | 301778 | 4 |  | 负载组 5 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 14 | 301778 | 4 |  | 负载组 5 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 15 | 301778 | 4 |  | 负载组 5 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 0 | 301778 | 4 |  | 负载组 5 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1777 | 1 | 301778 | 4 |  | 负载组 5 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 1 | 301779 | 4 |  | 负载组 6 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 2 | 301779 | 4 |  | 负载组 6 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 3 | 301779 | 4 |  | 负载组 6 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 4 | 301779 | 4 |  | 负载组 6 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 5 | 301779 | 4 |  | 负载组 6 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 6 | 301779 | 4 |  | 负载组 6 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 7 | 301779 | 4 |  | 负载组 6 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 8 | 301779 | 4 |  | 负载组 6 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 9 | 301779 | 4 |  | 负载组 6 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 10 | 301779 | 4 |  | 负载组 6 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 11 | 301779 | 4 |  | 负载组 6 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 12 | 301779 | 4 |  | 负载组 6 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 13 | 301779 | 4 |  | 负载组 6 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 14 | 301779 | 4 |  | 负载组 6 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 15 | 301779 | 4 |  | 负载组 6 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 0 | 301779 | 4 |  | 负载组 6 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1778 | 1 | 301779 | 4 |  | 负载组 6 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 1 | 301780 | 4 |  | 负载组 7 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 2 | 301780 | 4 |  | 负载组 7 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 3 | 301780 | 4 |  | 负载组 7 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 4 | 301780 | 4 |  | 负载组 7 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 5 | 301780 | 4 |  | 负载组 7 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 6 | 301780 | 4 |  | 负载组 7 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 7 | 301780 | 4 |  | 负载组 7 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 8 | 301780 | 4 |  | 负载组 7 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 9 | 301780 | 4 |  | 负载组 7 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 10 | 301780 | 4 |  | 负载组 7 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 11 | 301780 | 4 |  | 负载组 7 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 12 | 301780 | 4 |  | 负载组 7 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 13 | 301780 | 4 |  | 负载组 7 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 14 | 301780 | 4 |  | 负载组 7 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 15 | 301780 | 4 |  | 负载组 7 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 0 | 301780 | 4 |  | 负载组 7 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1779 | 1 | 301780 | 4 |  | 负载组 7 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 1 | 301781 | 4 |  | 负载组 8 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 2 | 301781 | 4 |  | 负载组 8 位置 ON - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 3 | 301781 | 4 |  | 负载组 8 位置 ON - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 4 | 301781 | 4 |  | 负载组 8 位置 ON - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 5 | 301781 | 4 |  | 负载组 8 位置 ON - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 6 | 301781 | 4 |  | 负载组 8 位置 ON - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 7 | 301781 | 4 |  | 负载组 8 位置 ON - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 8 | 301781 | 4 |  | 负载组 8 位置 ON - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 9 | 301781 | 4 |  | 负载组 8 位置 ON - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 10 | 301781 | 4 |  | 负载组 8 位置 ON - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 11 | 301781 | 4 |  | 负载组 8 位置 ON - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 12 | 301781 | 4 |  | 负载组 8 位置 ON - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 13 | 301781 | 4 |  | 负载组 8 位置 ON - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 14 | 301781 | 4 |  | 负载组 8 位置 ON - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 15 | 301781 | 4 |  | 负载组 8 位置 ON - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 0 | 301781 | 4 |  | 负载组 8 位置 ON - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1780 | 1 | 301781 | 4 |  | 负载组 8 位置 ON - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 1 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 2 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 3 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 4 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 5 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 6 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 7 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 8 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 9 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 10 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 11 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 12 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 13 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 14 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 15 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 0 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1781 | 1 | 301782 | 4 |  | 负载组 1 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 1 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 2 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 3 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 4 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 5 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 6 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 7 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 8 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 9 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 10 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 11 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 12 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 13 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 14 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 15 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 0 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1782 | 1 | 301783 | 4 |  | 负载组 2 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 1 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 2 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 3 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 4 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 5 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 6 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 7 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 8 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 9 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 10 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 11 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 12 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 13 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 14 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 15 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 0 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1783 | 1 | 301784 | 4 |  | 负载组 3 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 1 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 2 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 3 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 4 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 5 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 6 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 7 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 8 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 9 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 10 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 11 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 12 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 13 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 14 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 15 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 0 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1784 | 1 | 301785 | 4 |  | 负载组 4 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 1 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 2 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 3 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 4 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 5 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 6 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 7 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 8 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 9 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 10 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 11 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 12 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 13 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 14 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 15 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 0 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1785 | 1 | 301786 | 4 |  | 负载组 5 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 1 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 2 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 3 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 4 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 5 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 6 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 7 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 8 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 9 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 10 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 11 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 12 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 13 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 14 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 15 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 0 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1786 | 1 | 301787 | 4 |  | 负载组 6 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 1 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 2 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 3 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 4 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 5 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 6 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 7 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 8 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 9 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 10 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 11 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 12 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 13 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 14 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 15 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 0 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1787 | 1 | 301788 | 4 |  | 负载组 7 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 1 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 2 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 3 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 4 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 5 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 6 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 7 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 8 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 9 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 10 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 11 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 12 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 13 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 14 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 15 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 0 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1788 | 1 | 301789 | 4 |  | 负载组 8 位置 OFF - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 1 | 301790 | 4 |  | 负载组 1 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 2 | 301790 | 4 |  | 负载组 1 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 3 | 301790 | 4 |  | 负载组 1 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 4 | 301790 | 4 |  | 负载组 1 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 5 | 301790 | 4 |  | 负载组 1 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 6 | 301790 | 4 |  | 负载组 1 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 7 | 301790 | 4 |  | 负载组 1 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 8 | 301790 | 4 |  | 负载组 1 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 9 | 301790 | 4 |  | 负载组 1 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 10 | 301790 | 4 |  | 负载组 1 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 11 | 301790 | 4 |  | 负载组 1 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 12 | 301790 | 4 |  | 负载组 1 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 13 | 301790 | 4 |  | 负载组 1 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 14 | 301790 | 4 |  | 负载组 1 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 15 | 301790 | 4 |  | 负载组 1 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 0 | 301790 | 4 |  | 负载组 1 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1789 | 1 | 301790 | 4 |  | 负载组 1 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 1 | 301791 | 4 |  | 负载组 2 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 2 | 301791 | 4 |  | 负载组 2 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 3 | 301791 | 4 |  | 负载组 2 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 4 | 301791 | 4 |  | 负载组 2 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 5 | 301791 | 4 |  | 负载组 2 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 6 | 301791 | 4 |  | 负载组 2 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 7 | 301791 | 4 |  | 负载组 2 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 8 | 301791 | 4 |  | 负载组 2 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 9 | 301791 | 4 |  | 负载组 2 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 10 | 301791 | 4 |  | 负载组 2 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 11 | 301791 | 4 |  | 负载组 2 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 12 | 301791 | 4 |  | 负载组 2 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 13 | 301791 | 4 |  | 负载组 2 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 14 | 301791 | 4 |  | 负载组 2 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 15 | 301791 | 4 |  | 负载组 2 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 0 | 301791 | 4 |  | 负载组 2 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1790 | 1 | 301791 | 4 |  | 负载组 2 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 1 | 301792 | 4 |  | 负载组 3 激活- ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 2 | 301792 | 4 |  | 负载组 3 激活- ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 3 | 301792 | 4 |  | 负载组 3 激活- ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 4 | 301792 | 4 |  | 负载组 3 激活- ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 5 | 301792 | 4 |  | 负载组 3 激活- ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 6 | 301792 | 4 |  | 负载组 3 激活- ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 7 | 301792 | 4 |  | 负载组 3 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 8 | 301792 | 4 |  | 负载组 3 激活- ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 9 | 301792 | 4 |  | 负载组 3 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 10 | 301792 | 4 |  | 负载组 3 激活- ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 11 | 301792 | 4 |  | 负载组 3 激活- ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 12 | 301792 | 4 |  | 负载组 3 激活- ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 13 | 301792 | 4 |  | 负载组 3 激活- ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 14 | 301792 | 4 |  | 负载组 3 激活- ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 15 | 301792 | 4 |  | 负载组 3 激活- ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 0 | 301792 | 4 |  | 负载组 3 激活- ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1791 | 1 | 301792 | 4 |  | 负载组 3 激活- ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 1 | 301793 | 4 |  | 负载组 4 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 2 | 301793 | 4 |  | 负载组 4 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 3 | 301793 | 4 |  | 负载组 4 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 4 | 301793 | 4 |  | 负载组 4 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 5 | 301793 | 4 |  | 负载组 4 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 6 | 301793 | 4 |  | 负载组 4 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 7 | 301793 | 4 |  | 负载组 4 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 8 | 301793 | 4 |  | 负载组 4 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 9 | 301793 | 4 |  | 负载组 4 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 10 | 301793 | 4 |  | 负载组 4 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 11 | 301793 | 4 |  | 负载组 4 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 12 | 301793 | 4 |  | 负载组 4 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 13 | 301793 | 4 |  | 负载组 4 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 14 | 301793 | 4 |  | 负载组 4 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 15 | 301793 | 4 |  | 负载组 4 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 0 | 301793 | 4 |  | 负载组 4 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1792 | 1 | 301793 | 4 |  | 负载组 4 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 1 | 301794 | 4 |  | 负载组 5 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 2 | 301794 | 4 |  | 负载组 5 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 3 | 301794 | 4 |  | 负载组 5 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 4 | 301794 | 4 |  | 负载组 5 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 5 | 301794 | 4 |  | 负载组 5 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 6 | 301794 | 4 |  | 负载组 5 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 7 | 301794 | 4 |  | 负载组 5 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 8 | 301794 | 4 |  | 负载组 5 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 9 | 301794 | 4 |  | 负载组 5 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 10 | 301794 | 4 |  | 负载组 5 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 11 | 301794 | 4 |  | 负载组 5 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 12 | 301794 | 4 |  | 负载组 5 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 13 | 301794 | 4 |  | 负载组 5 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 14 | 301794 | 4 |  | 负载组 5 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 15 | 301794 | 4 |  | 负载组 5 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 0 | 301794 | 4 |  | 负载组 5 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1793 | 1 | 301794 | 4 |  | 负载组 5 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 1 | 301795 | 4 |  | 负载组 6 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 2 | 301795 | 4 |  | 负载组 6 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 3 | 301795 | 4 |  | 负载组 6 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 4 | 301795 | 4 |  | 负载组 6 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 5 | 301795 | 4 |  | 负载组 6 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 6 | 301795 | 4 |  | 负载组 6 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 7 | 301795 | 4 |  | 负载组 6 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 8 | 301795 | 4 |  | 负载组 6 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 9 | 301795 | 4 |  | 负载组 6 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 10 | 301795 | 4 |  | 负载组 6 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 11 | 301795 | 4 |  | 负载组 6 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 12 | 301795 | 4 |  | 负载组 6 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 13 | 301795 | 4 |  | 负载组 6 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 14 | 301795 | 4 |  | 负载组 6 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 15 | 301795 | 4 |  | 负载组 6 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 0 | 301795 | 4 |  | 负载组 6 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1794 | 1 | 301795 | 4 |  | 负载组 6 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 1 | 301796 | 4 |  | 负载组 7 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 2 | 301796 | 4 |  | 负载组 7 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 3 | 301796 | 4 |  | 负载组 7 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 4 | 301796 | 4 |  | 负载组 7 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 5 | 301796 | 4 |  | 负载组 7 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 6 | 301796 | 4 |  | 负载组 7 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 7 | 301796 | 4 |  | 负载组 7 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 8 | 301796 | 4 |  | 负载组 7 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 9 | 301796 | 4 |  | 负载组 7 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 10 | 301796 | 4 |  | 负载组 7 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 11 | 301796 | 4 |  | 负载组 7 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 12 | 301796 | 4 |  | 负载组 7 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 13 | 301796 | 4 |  | 负载组 7 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 14 | 301796 | 4 |  | 负载组 7 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 15 | 301796 | 4 |  | 负载组 7 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 0 | 301796 | 4 |  | 负载组 7 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1795 | 1 | 301796 | 4 |  | 负载组 7 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 1 | 301797 | 4 |  | 负载组 8 激活 - ID 33 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 2 | 301797 | 4 |  | 负载组 8 激活 - ID 34 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 3 | 301797 | 4 |  | 负载组 8 激活 - ID 35 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 4 | 301797 | 4 |  | 负载组 8 激活 - ID 36 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 5 | 301797 | 4 |  | 负载组 8 激活 - ID 37 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 6 | 301797 | 4 |  | 负载组 8 激活 - ID 38 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 7 | 301797 | 4 |  | 负载组 8 激活 - ID 39 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 8 | 301797 | 4 |  | 负载组 8 激活 - ID 40 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 9 | 301797 | 4 |  | 负载组 8 激活 - ID 25 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 10 | 301797 | 4 |  | 负载组 8 激活 - ID 26 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 11 | 301797 | 4 |  | 负载组 8 激活 - ID 27 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 12 | 301797 | 4 |  | 负载组 8 激活 - ID 28 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 13 | 301797 | 4 |  | 负载组 8 激活 - ID 29 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 14 | 301797 | 4 |  | 负载组 8 激活 - ID 30 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 15 | 301797 | 4 |  | 负载组 8 激活 - ID 31 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 0 | 301797 | 4 |  | 负载组 8 激活 - ID 32 | BOOL |  |  |  | X | X | X
PM报警 | 1796 | 1 | 301797 | 4 |  | 负载组 8 激活 - ID 33 | BOOL |  |  |  | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on C4: Bit location of the function in the associated Modbus address.
Note on E4: 04 - Read single or multiple
Note on F4: The parameter number of the function.
Note on G4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on I4: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on J4: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on K4: Unit of the associated function
Note on L4: Indicates if the address is available in the BUS TIE breaker controller.
Note on M4: Indicates if the address is available in the MAINS controller.
Note on N4: Indicates if the address is available in the GENSET controller.